## 5 minutes
Time range: | 2026-06-02 00:00:00 - 2026-06-02 23:59:59
Export time: | 2026-06-03 00:03:09
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge energy(kWh) | Total discharge energy(kWh) | Daily auxiliary power consumption(kWh) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge power(kW) | SOC(%) | Equivalent number of cycles | Battery cabin temperature 1(℃) | Battery cabin humidity 1(%) | Battery cabin temperature 2(℃) | Battery cabin humidity 2(%) | CO concentration 1(ppm) | CO concentration 2(ppm) | H2 concentration 1(ppm) | H2 concentration 2(ppm) | Control unit cabin temperature 1(℃) | Control unit cabin humidity 1(%) | Control status of EEV 1(step) | Control status of EEV 2(step) | Running status of outdoor fan 1(%) | Running status of outdoor fan 2(%) | Discharge temperature of compressor 1(℃) | Suction temperature of refrigerant system 1(℃) | Condenser outlet temperature of refrigerant system 1(℃) | Condenser outlet pressure of refrigerant system 1(Mpa) | Suction superheat degree of refrigerant system 1(℃) | Discharge superheat degree of compressor 1(℃) | Running status of outdoor fan 3(%) | Discharge temperature of compressor 2(℃) | Suction temperature of refrigerant system 2(℃) | Condenser outlet temperature of refrigerant system 2(℃) | Condenser outlet pressure of refrigerant system 2(Mpa) | Suction superheat degree of refrigerant system 2(℃) | Discharge superheat degree of compressor 2(℃) | Battery-side supply water temperature(℃) | Battery-side return water temperature(℃) | Air intake temperature(℃) | Discharge pressure of refrigerant system 1(Mpa) | Suction pressure of refrigerant system 1(Mpa) | Discharge pressure of refrigerant system 2(Mpa) | Suction pressure of refrigerant system 2(Mpa) | Running status of EEV 1(step) | Running status of EEV 2(step) | Compressor 1 running status(rpm) | Compressor 2 running status(rpm)
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:00:00 | 0 | 0 | 783204.32 | 755375.72 | 0 | 4226.823 | 246.003 | -10.9 | 6 | 175 | 26 | 52.2 | 26.1 | 52 | 0 | 0 | - | - | 29.9 | 46.3 | 0 | 0 | 0 | 0 | 28 | 29.7 | 27.7 | 1.47 | 5.4 | 3.9 | 0 | 27.6 | 28.8 | 27.5 | 1.48 | 4.4 | 3.7 | 24.1 | 24.1 | 26.6 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:05:00 | 0.04 | 0.78 | 783204.32 | 755376.52 | 0.1 | 4226.823 | 246.003 | -12.019 | 6 | 175 | 26 | 52.2 | 26.1 | 52 | 0 | 0 | - | - | 29.9 | 46.3 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 27.8 | 1.47 | 5.4 | 3.9 | 0 | 27.7 | 28.8 | 27.5 | 1.48 | 4.4 | 3.7 | 24.1 | 24.1 | 26.6 | 1.51 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:10:00 | 0.04 | 1.48 | 783204.32 | 755377.24 | 0.2 | 4226.823 | 246.003 | -10.051 | 6 | 175 | 26 | 52.3 | 26.1 | 52 | 0 | 0 | - | - | 29.9 | 46.4 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 27.9 | 1.47 | 5.4 | 4 | 0 | 27.7 | 28.8 | 27.5 | 1.48 | 4.5 | 3.8 | 24.2 | 24.1 | 26.7 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:15:00 | 0.08 | 2.18 | 783204.36 | 755377.9 | 0.3 | 4264.098 | 208.728 | -5.862 | 6 | 175 | 26 | 52.3 | 26.1 | 52 | 0 | 0 | - | - | 29.9 | 46.4 | 0 | 0 | 0 | 0 | 28.3 | 29.7 | 27.9 | 1.47 | 5.4 | 4 | 0 | 27.7 | 28.9 | 27.6 | 1.48 | 4.4 | 3.8 | 24.2 | 24.2 | 26.7 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:20:00 | 0.08 | 2.86 | 783204.36 | 755378.58 | 0.4 | 4234.278 | 238.548 | -6.974 | 5 | 175 | 26 | 52.3 | 26.1 | 52 | 0 | 0 | - | - | 29.8 | 46.4 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 27.9 | 1.47 | 5.3 | 4 | 0 | 27.8 | 28.9 | 27.6 | 1.48 | 4.5 | 3.8 | 24.2 | 24.2 | 26.8 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:25:00 | 0.12 | 3.86 | 783204.4 | 755379.58 | 0.5 | 4234.278 | 238.548 | -9.587 | 5 | 175 | 26 | 52.3 | 26.1 | 52 | 0 | 0 | - | - | 29.8 | 46.4 | 0 | 0 | 0 | 0 | 28.3 | 29.7 | 27.9 | 1.47 | 5.3 | 4.1 | 0 | 27.8 | 28.9 | 27.6 | 1.48 | 4.5 | 3.9 | 24.2 | 24.2 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:30:00 | 0.2 | 4.74 | 783204.48 | 755380.48 | 0.6 | 4264.098 | 208.728 | -8.991 | 5 | 175 | 26 | 52.3 | 26.1 | 52 | 0 | 0 | - | - | 29.8 | 46.4 | 0 | 0 | 0 | 0 | 28.2 | 29.6 | 27.8 | 1.47 | 5.1 | 3.9 | 0 | 27.8 | 28.9 | 27.6 | 1.48 | 4.4 | 3.8 | 24.2 | 24.2 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:35:00 | 0.2 | 5.56 | 783204.48 | 755381.32 | 0.69 | 4264.098 | 208.728 | -11.375 | 5 | 175 | 26 | 52.3 | 26.1 | 52 | 0 | 0 | - | - | 29.8 | 46.4 | 0 | 0 | 0 | 0 | 28.2 | 29.5 | 27.8 | 1.47 | 5 | 3.9 | 0 | 27.8 | 28.8 | 27.6 | 1.49 | 4.3 | 3.8 | 24.2 | 24.2 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:40:00 | 0.24 | 6.38 | 783204.52 | 755382.12 | 0.79 | 4241.733 | 231.093 | -11.077 | 5 | 175 | 26 | 52.3 | 26.1 | 52 | 0 | 0 | - | - | 29.7 | 46.4 | 0 | 0 | 0 | 0 | 28.2 | 29.4 | 27.7 | 1.47 | 5 | 3.9 | 0 | 27.8 | 28.8 | 27.5 | 1.49 | 4.3 | 3.8 | 24.2 | 24.2 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:45:00 | 0.24 | 7.12 | 783204.52 | 755382.86 | 0.88 | 4264.098 | 208.728 | -14.414 | 5 | 175 | 26 | 52.3 | 26.1 | 52 | 0 | 0 | - | - | 29.7 | 46.5 | 0 | 0 | 0 | 0 | 28.3 | 29.4 | 27.8 | 1.47 | 5 | 4 | 0 | 27.8 | 28.8 | 27.5 | 1.49 | 4.3 | 3.8 | 24.3 | 24.2 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:50:00 | 0.3 | 8.04 | 783204.58 | 755383.78 | 0.97 | 4264.098 | 208.728 | -12.837 | 5 | 175 | 26 | 52.3 | 26.1 | 52 | 0 | 0 | - | - | 29.7 | 46.5 | 0 | 0 | 0 | 0 | 28.2 | 29.4 | 27.8 | 1.47 | 5 | 4 | 0 | 27.8 | 28.7 | 27.5 | 1.49 | 4.2 | 3.8 | 24.3 | 24.2 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 00:55:00 | 0.34 | 8.88 | 783204.62 | 755384.64 | 1.06 | 4264.098 | 208.728 | -9.774 | 5 | 175 | 26.1 | 52.3 | 26.1 | 52.1 | 0 | 0 | - | - | 29.7 | 46.6 | 0 | 0 | 0 | 0 | 28.2 | 29.3 | 27.9 | 1.47 | 4.9 | 3.9 | 0 | 27.8 | 28.7 | 27.5 | 1.49 | 4.2 | 3.7 | 24.3 | 24.2 | 26.6 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:00:00 | 0.34 | 9.66 | 783204.62 | 755385.38 | 1.15 | 4264.098 | 208.728 | -10.081 | 5 | 175 | 26.1 | 52.3 | 26 | 52.3 | 0 | 0 | - | - | 29.7 | 46.6 | 0 | 0 | 0 | 0 | 28.2 | 29.3 | 27.9 | 1.47 | 4.8 | 3.9 | 0 | 27.8 | 28.7 | 27.6 | 1.49 | 4.1 | 3.7 | 24.3 | 24.3 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:05:00 | 0.4 | 10.42 | 783204.68 | 755386.18 | 1.24 | 4249.188 | 223.638 | -30.659 | 5 | 175 | 26.1 | 52.3 | 26 | 52.3 | 0 | 0 | - | - | 29.6 | 46.6 | 0 | 0 | 0 | 0 | 28.2 | 29.2 | 27.9 | 1.47 | 4.8 | 4 | 0 | 27.8 | 28.7 | 27.6 | 1.49 | 4.1 | 3.7 | 24.3 | 24.3 | 26.6 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:10:00 | 0.46 | 11.24 | 783204.74 | 755386.96 | 1.33 | 4256.643 | 216.183 | -13.328 | 5 | 175 | 26.1 | 52.3 | 26.1 | 52.2 | 0 | 0 | - | - | 29.6 | 46.7 | 0 | 0 | 0 | 0 | 28.3 | 29.2 | 28.1 | 1.47 | 4.8 | 4 | 0 | 27.8 | 28.6 | 27.6 | 1.49 | 4 | 3.7 | 24.3 | 24.3 | 26.6 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:15:00 | 0.46 | 12.16 | 783204.74 | 755387.88 | 1.42 | 4264.098 | 208.728 | 22.151 | 5 | 175 | 26.1 | 52.3 | 26.1 | 52.1 | 0 | 0 | - | - | 29.6 | 46.7 | 0 | 0 | 0 | 0 | 28.3 | 29.2 | 28.1 | 1.47 | 4.8 | 4 | 0 | 27.8 | 28.6 | 27.6 | 1.49 | 4.1 | 3.7 | 24.3 | 24.3 | 26.6 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:20:00 | 0.48 | 12.92 | 783204.76 | 755388.64 | 1.55 | 4264.098 | 208.728 | -10.425 | 5 | 175 | 26.1 | 52.3 | 26.2 | 52.1 | 0 | 0 | - | - | 29.6 | 46.7 | 0 | 0 | -59.7 | -60 | 28.2 | 29.2 | 27.9 | 1.48 | 4.6 | 3.8 | -59.9 | 27.7 | 28.7 | 27.7 | 1.49 | 4 | 3.5 | 24.3 | 24.3 | 26.5 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:25:00 | 0.58 | 13.76 | 783204.86 | 755389.52 | 1.64 | 4264.098 | 208.728 | -10.111 | 5 | 175 | 26.1 | 52.3 | 26.1 | 52.2 | 0 | 0 | - | - | 29.6 | 46.7 | 0 | 0 | 0 | 0 | 27.7 | 29.2 | 27.8 | 1.48 | 4.6 | 3.2 | 0 | 27.3 | 29.1 | 27.7 | 1.49 | 4.4 | 3.1 | 24.4 | 24.4 | 26.6 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:30:00 | 0.58 | 14.68 | 783204.86 | 755390.4 | 1.73 | 4264.098 | 208.728 | -9.884 | 5 | 175 | 26.1 | 52.3 | 26.1 | 52.2 | 0 | 0 | - | - | 29.6 | 46.7 | 0 | 0 | 0 | 0 | 27.7 | 29.1 | 28 | 1.48 | 4.6 | 3.3 | 0 | 27.3 | 28.9 | 27.7 | 1.49 | 4.3 | 3.2 | 24.4 | 24.3 | 26.4 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:35:00 | 0.68 | 15.48 | 783204.96 | 755391.2 | 1.82 | 4271.553 | 201.273 | -12.54 | 5 | 175 | 26.1 | 52.3 | 26.2 | 52.1 | 0 | 0 | - | - | 29.6 | 46.7 | 0 | 0 | 0 | 0 | 27.8 | 29.1 | 28.1 | 1.48 | 4.6 | 3.5 | 0 | 27.4 | 28.8 | 27.7 | 1.49 | 4.2 | 3.2 | 24.4 | 24.3 | 26.5 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:40:00 | 0.7 | 16.34 | 783204.98 | 755392.06 | 1.9 | 4249.188 | 223.638 | -10.385 | 5 | 175 | 26.1 | 52.3 | 26.2 | 52.1 | 0 | 0 | - | - | 29.6 | 46.8 | 0 | 0 | 0 | 0 | 28 | 29.1 | 28.1 | 1.48 | 4.5 | 3.7 | 0 | 27.5 | 28.7 | 27.7 | 1.49 | 4.1 | 3.3 | 24.4 | 24.4 | 26.6 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:45:00 | 0.74 | 17.12 | 783205.02 | 755392.84 | 1.99 | 4271.553 | 201.273 | -9.148 | 5 | 175 | 26.1 | 52.3 | 26.2 | 52.1 | 0 | 0 | - | - | 29.6 | 46.8 | 0 | 0 | 0 | 0 | 28.1 | 29.1 | 28.2 | 1.48 | 4.6 | 3.7 | 0 | 27.6 | 28.7 | 27.7 | 1.49 | 4 | 3.4 | 24.4 | 24.4 | 26.5 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:50:00 | 0.8 | 17.94 | 783205.08 | 755393.7 | 2.07 | 4249.188 | 223.638 | -9.399 | 5 | 175 | 26.1 | 52.3 | 26.2 | 52 | 0 | 0 | - | - | 29.6 | 46.8 | 0 | 0 | 0 | 0 | 28.2 | 29.1 | 28.2 | 1.48 | 4.5 | 3.8 | 0 | 27.7 | 28.7 | 27.8 | 1.49 | 4 | 3.5 | 24.4 | 24.4 | 26.4 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 01:55:00 | 0.82 | 18.82 | 783205.1 | 755394.54 | 2.16 | 4279.009 | 193.818 | -11.974 | 5 | 175 | 26.1 | 52.3 | 26.3 | 52 | 0 | 0 | - | - | 29.6 | 46.8 | 0 | 0 | 0 | 0 | 28.3 | 29.1 | 28.2 | 1.48 | 4.5 | 3.9 | 0 | 27.7 | 28.7 | 27.9 | 1.49 | 3.9 | 3.5 | 24.4 | 24.4 | 26.4 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:00:00 | 0.82 | 19.68 | 783205.1 | 755395.42 | 2.25 | 4279.009 | 193.818 | -7.137 | 5 | 175 | 26.1 | 52.3 | 26.3 | 52 | 0 | 0 | - | - | 29.6 | 46.8 | 0 | 0 | 0 | 0 | 28.4 | 29.1 | 28.3 | 1.48 | 4.5 | 4 | 0 | 27.8 | 28.6 | 27.9 | 1.49 | 3.9 | 3.6 | 24.5 | 24.4 | 26.4 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:05:00 | 0.86 | 20.46 | 783205.14 | 755396.18 | 2.33 | 4279.009 | 193.818 | -10.678 | 5 | 175 | 26.1 | 52.3 | 26.3 | 52 | 0 | 0 | - | - | 29.6 | 46.8 | 0 | 0 | 0 | 0 | 28.4 | 29 | 28.3 | 1.48 | 4.4 | 4 | 0 | 27.8 | 28.6 | 27.9 | 1.5 | 3.9 | 3.6 | 24.4 | 24.4 | 26.4 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:10:00 | 0.86 | 21.16 | 783205.14 | 755396.88 | 2.42 | 4249.188 | 223.638 | -9.448 | 5 | 175 | 26.1 | 52.3 | 26.3 | 52 | 0 | 0 | - | - | 29.6 | 46.8 | 0 | 0 | 0 | 0 | 28.5 | 29 | 28.4 | 1.48 | 4.4 | 4 | 0 | 27.8 | 28.6 | 27.9 | 1.5 | 3.8 | 3.6 | 24.5 | 24.4 | 26.5 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:15:00 | 0.94 | 21.94 | 783205.22 | 755397.66 | 2.5 | 4279.009 | 193.818 | -9.262 | 5 | 175 | 26.1 | 52.3 | 26.3 | 52 | 0 | 0 | - | - | 29.6 | 46.9 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.4 | 1.48 | 4.3 | 4 | 0 | 27.8 | 28.6 | 27.9 | 1.5 | 3.8 | 3.6 | 24.5 | 24.4 | 26.5 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:20:00 | 0.98 | 22.82 | 783205.28 | 755398.54 | 2.59 | 4279.009 | 193.818 | -8.546 | 5 | 175 | 26.1 | 52.3 | 26.3 | 52 | 0 | 0 | - | - | 29.6 | 46.9 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.4 | 1.48 | 4.3 | 3.9 | 0 | 27.8 | 28.6 | 27.9 | 1.5 | 3.8 | 3.6 | 24.5 | 24.5 | 26.4 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:25:00 | 1.06 | 23.52 | 783205.34 | 755399.24 | 2.67 | 4249.188 | 223.638 | -9.877 | 5 | 175 | 26.1 | 52.3 | 26.3 | 52 | 0 | 0 | - | - | 29.5 | 46.9 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.3 | 1.48 | 4.3 | 4 | 0 | 27.8 | 28.5 | 27.9 | 1.5 | 3.8 | 3.6 | 24.5 | 24.5 | 26.5 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:30:00 | 1.06 | 24.18 | 783205.34 | 755399.9 | 2.76 | 4249.188 | 223.638 | -9.377 | 5 | 175 | 26.1 | 52.3 | 26.3 | 52 | 0 | 0 | - | - | 29.5 | 47 | 0 | 0 | 0 | 0 | 28.4 | 29 | 28.4 | 1.48 | 4.3 | 4 | 0 | 27.9 | 28.4 | 27.9 | 1.5 | 3.7 | 3.6 | 24.5 | 24.5 | 26.6 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:35:00 | 1.06 | 24.82 | 783205.34 | 755400.54 | 2.84 | 4249.188 | 223.638 | -8.31 | 5 | 175 | 26.2 | 52.4 | 26.3 | 52 | 0 | 0 | - | - | 29.5 | 47 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.4 | 1.48 | 4.2 | 4 | 0 | 27.9 | 28.4 | 27.9 | 1.5 | 3.7 | 3.6 | 24.6 | 24.5 | 26.6 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:40:00 | 1.06 | 25.46 | 783205.34 | 755401.2 | 2.93 | 4249.188 | 223.638 | -11.666 | 5 | 175 | 26.2 | 52.4 | 26.3 | 52.1 | 0 | 0 | - | - | 29.5 | 47 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.3 | 1.48 | 4.3 | 4 | 0 | 27.9 | 28.4 | 27.9 | 1.5 | 3.7 | 3.5 | 24.6 | 24.5 | 26.6 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:45:00 | 1.06 | 26.12 | 783205.34 | 755401.88 | 3.01 | 4249.188 | 223.638 | -9.359 | 5 | 175 | 26.2 | 52.4 | 26.3 | 52.1 | 0 | 0 | - | - | 29.5 | 47 | 0 | 0 | 0 | 0 | 28.5 | 28.9 | 28.4 | 1.48 | 4.3 | 4 | 0 | 27.9 | 28.4 | 27.9 | 1.5 | 3.6 | 3.6 | 24.6 | 24.6 | 26.5 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:50:00 | 1.08 | 26.86 | 783205.36 | 755402.58 | 3.09 | 4249.188 | 223.638 | -8.914 | 5 | 175 | 26.2 | 52.4 | 26.4 | 52 | 0 | 0 | - | - | 29.5 | 47 | 0 | 0 | 0 | 0 | 28.6 | 28.9 | 28.3 | 1.48 | 4.3 | 4.2 | 0 | 28 | 28.5 | 28 | 1.5 | 3.7 | 3.7 | 24.6 | 24.6 | 26.3 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 02:55:00 | 1.1 | 27.52 | 783205.38 | 755403.26 | 3.18 | 4293.918 | 178.908 | 13.162 | 5 | 175 | 26.2 | 52.4 | 26.4 | 52 | 0 | 0 | - | - | 29.5 | 47 | 0 | 0 | 0 | 0 | 28.7 | 28.9 | 28.4 | 1.48 | 4.3 | 4.2 | 0 | 28 | 28.5 | 28.1 | 1.5 | 3.6 | 3.7 | 24.6 | 24.6 | 26.4 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:00:00 | 1.18 | 28.2 | 783205.46 | 755403.94 | 3.27 | 4264.098 | 208.728 | -13.263 | 5 | 175 | 26.2 | 52.4 | 26.4 | 52 | 0 | 0 | - | - | 29.5 | 47 | 0 | 0 | 0 | 0 | 28.7 | 28.9 | 28.5 | 1.48 | 4.3 | 4.2 | 0 | 28.1 | 28.4 | 28.2 | 1.5 | 3.6 | 3.7 | 24.6 | 24.6 | 26.3 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:05:00 | 1.18 | 28.8 | 783205.46 | 755404.52 | 3.35 | 4264.098 | 208.728 | -10.875 | 5 | 175 | 26.2 | 52.4 | 26.4 | 52 | 0 | 0 | - | - | 29.5 | 47.1 | 0 | 0 | 0 | 0 | 28.8 | 28.9 | 28.6 | 1.48 | 4.3 | 4.3 | 0 | 28.1 | 28.4 | 28.2 | 1.5 | 3.6 | 3.7 | 24.6 | 24.6 | 26.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:10:00 | 1.18 | 29.46 | 783205.46 | 755405.18 | 3.44 | 4264.098 | 208.728 | -9.065 | 5 | 175 | 26.2 | 52.4 | 26.4 | 52.1 | 0 | 0 | - | - | 29.5 | 47.1 | 0 | 0 | 0 | 0 | 28.8 | 28.9 | 28.6 | 1.48 | 4.3 | 4.4 | 0 | 28.1 | 28.5 | 28.3 | 1.5 | 3.6 | 3.8 | 24.7 | 24.6 | 26.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:15:00 | 1.18 | 30.12 | 783205.46 | 755405.84 | 3.53 | 4264.098 | 208.728 | -10.073 | 5 | 175 | 26.2 | 52.4 | 26.4 | 52.1 | 0 | 0 | - | - | 29.5 | 47.1 | 0 | 0 | 0 | 0 | 28.9 | 29 | 28.7 | 1.48 | 4.4 | 4.5 | 0 | 28.2 | 28.5 | 28.3 | 1.5 | 3.6 | 3.8 | 24.7 | 24.7 | 26.3 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:20:00 | 1.18 | 30.7 | 783205.46 | 755406.44 | 3.62 | 4264.098 | 208.728 | -11.262 | 5 | 175 | 26.2 | 52.4 | 26.4 | 52.1 | 0 | 0 | - | - | 29.5 | 47.1 | 0 | 0 | 0 | 0 | 29 | 29 | 28.7 | 1.48 | 4.4 | 4.5 | 0 | 28.2 | 28.5 | 28.4 | 1.5 | 3.6 | 3.8 | 24.7 | 24.7 | 26.2 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:25:00 | 1.2 | 31.2 | 783205.48 | 755406.92 | 3.71 | 4264.098 | 208.728 | -35.316 | 5 | 175 | 26.2 | 52.4 | 26.4 | 52.1 | 0 | 0 | - | - | 29.5 | 47.1 | 0 | 0 | 0 | 0 | 29 | 29.1 | 28.9 | 1.48 | 4.4 | 4.5 | 0 | 28.3 | 28.6 | 28.5 | 1.5 | 3.7 | 3.9 | 24.7 | 24.7 | 26.3 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:30:00 | 1.32 | 32 | 783205.6 | 755407.76 | 3.8 | 4293.918 | 178.908 | -9.662 | 5 | 175 | 26.2 | 52.4 | 26.4 | 52.1 | 0 | 0 | - | - | 29.6 | 47.1 | 0 | 0 | 0 | 0 | 29.1 | 29.2 | 28.9 | 1.48 | 4.5 | 4.5 | 0 | 28.3 | 28.6 | 28.6 | 1.5 | 3.7 | 3.9 | 24.7 | 24.7 | 26.5 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:35:00 | 1.32 | 32.68 | 783205.6 | 755408.4 | 3.89 | 4264.098 | 208.728 | -9.711 | 5 | 175 | 26.2 | 52.4 | 26.5 | 52 | 0 | 0 | - | - | 29.6 | 47.1 | 0 | 0 | 0 | 0 | 29.1 | 29.2 | 28.8 | 1.48 | 4.5 | 4.5 | 0 | 28.3 | 28.7 | 28.6 | 1.5 | 3.7 | 3.9 | 24.7 | 24.7 | 26.7 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:40:00 | 1.36 | 33.42 | 783205.64 | 755409.14 | 3.98 | 4264.098 | 208.728 | -13.173 | 5 | 175 | 26.3 | 52.4 | 26.5 | 52 | 0 | 0 | - | - | 29.6 | 47.1 | 0 | 0 | 0 | 0 | 29.1 | 29.2 | 28.9 | 1.48 | 4.5 | 4.5 | 0 | 28.3 | 28.7 | 28.7 | 1.5 | 3.8 | 3.9 | 24.7 | 24.7 | 26.6 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:45:00 | 1.36 | 34.06 | 783205.64 | 755409.8 | 4.07 | 4264.098 | 208.728 | -11.325 | 5 | 175 | 26.3 | 52.4 | 26.5 | 52 | 0 | 0 | - | - | 29.6 | 47.1 | 0 | 0 | 0 | 0 | 29.2 | 29.3 | 28.9 | 1.49 | 4.6 | 4.5 | 0 | 28.3 | 28.7 | 28.7 | 1.51 | 3.7 | 3.8 | 24.8 | 24.7 | 26.7 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:50:00 | 1.38 | 34.78 | 783205.66 | 755410.52 | 4.16 | 4264.098 | 208.728 | -8.962 | 5 | 175 | 26.3 | 52.4 | 26.5 | 52 | 0 | 0 | - | - | 29.6 | 47.2 | 0 | 0 | 0 | 0 | 29.2 | 29.2 | 28.8 | 1.49 | 4.5 | 4.5 | 0 | 28.3 | 28.7 | 28.7 | 1.51 | 3.7 | 3.8 | 24.8 | 24.7 | 26.8 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 03:55:00 | 1.4 | 35.52 | 783205.68 | 755411.26 | 4.25 | 4293.917 | 178.909 | -6.429 | 5 | 175 | 26.3 | 52.4 | 26.5 | 52 | 0 | 0 | - | - | 29.6 | 47.2 | 0 | 0 | 0 | 0 | 29.1 | 29.2 | 28.7 | 1.49 | 4.5 | 4.4 | 0 | 28.2 | 28.7 | 28.7 | 1.51 | 3.7 | 3.7 | 24.8 | 24.8 | 26.8 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:00:00 | 1.4 | 36.18 | 783205.68 | 755411.92 | 4.34 | 4264.098 | 208.728 | -9.242 | 5 | 175 | 26.3 | 52.4 | 26.5 | 52.1 | 0 | 0 | - | - | 29.6 | 47.2 | 0 | 0 | 0 | 0 | 28.8 | 29.2 | 28.5 | 1.49 | 4.4 | 4.2 | 0 | 28.2 | 28.7 | 28.7 | 1.51 | 3.6 | 3.6 | 24.8 | 24.8 | 26.7 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:05:00 | 1.4 | 36.88 | 783205.68 | 755412.6 | 4.43 | 4271.553 | 201.273 | -9.445 | 5 | 175 | 26.3 | 52.4 | 26.5 | 52.1 | 0 | 0 | - | - | 29.6 | 47.2 | 0 | 0 | 0 | 0 | 28.8 | 29.2 | 28.3 | 1.49 | 4.4 | 4.1 | 0 | 28.1 | 28.6 | 28.6 | 1.51 | 3.5 | 3.5 | 24.8 | 24.7 | 26.7 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:10:00 | 1.44 | 37.66 | 783205.72 | 755413.4 | 4.51 | 4308.826 | 164 | -9.06 | 5 | 175 | 26.3 | 52.4 | 26.5 | 52.1 | 0 | 0 | - | - | 29.6 | 47.3 | 0 | 0 | 0 | 0 | 28.7 | 29.2 | 28.2 | 1.49 | 4.3 | 3.9 | 0 | 27.9 | 28.5 | 28.4 | 1.51 | 3.4 | 3.4 | 24.8 | 24.8 | 26.7 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:15:00 | 1.48 | 38.32 | 783205.76 | 755414.1 | 4.6 | 4271.553 | 201.273 | -45.112 | 5 | 175 | 26.3 | 52.5 | 26.5 | 52.1 | 0 | 0 | - | - | 29.6 | 47.3 | 0 | 0 | 0 | 0 | 28.6 | 29.1 | 28.3 | 1.49 | 4.3 | 4 | 0 | 27.9 | 28.4 | 28.4 | 1.51 | 3.4 | 3.4 | 24.8 | 24.8 | 26.8 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:20:00 | 1.48 | 39.06 | 783205.76 | 755414.82 | 4.68 | 4286.463 | 186.364 | -9.512 | 5 | 175 | 26.3 | 52.5 | 26.5 | 52.1 | 0 | 0 | - | - | 29.6 | 47.3 | 0 | 0 | 0 | 0 | 28.8 | 29.2 | 28.4 | 1.49 | 4.3 | 4.1 | 0 | 28 | 28.4 | 28.4 | 1.51 | 3.4 | 3.4 | 24.8 | 24.8 | 26.7 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:25:00 | 1.48 | 39.74 | 783205.76 | 755415.46 | 4.77 | 4271.553 | 201.273 | -10.979 | 5 | 175 | 26.3 | 52.5 | 26.6 | 52.1 | 0 | 0 | - | - | 29.6 | 47.3 | 0 | 0 | 0 | 0 | 28.8 | 29.2 | 28.6 | 1.49 | 4.3 | 4.1 | 0 | 28 | 28.5 | 28.4 | 1.51 | 3.5 | 3.4 | 24.8 | 24.8 | 26.7 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:30:00 | 1.48 | 40.34 | 783205.76 | 755416.06 | 4.86 | 4271.553 | 201.273 | -12.778 | 5 | 175 | 26.3 | 52.5 | 26.6 | 52.1 | 0 | 0 | - | - | 29.5 | 47.4 | 0 | 0 | 0 | 0 | 28.8 | 29.1 | 28.7 | 1.49 | 4.2 | 4.1 | 0 | 28 | 28.5 | 28.3 | 1.51 | 3.4 | 3.4 | 24.9 | 24.8 | 26.8 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:35:00 | 1.48 | 41.12 | 783205.76 | 755416.84 | 4.94 | 4308.826 | 164 | -10.169 | 5 | 175 | 26.3 | 52.5 | 26.6 | 52.1 | 0 | 0 | - | - | 29.6 | 47.4 | 0 | 0 | 0 | 0 | 28.8 | 29.1 | 28.6 | 1.49 | 4.2 | 4.1 | 0 | 28.1 | 28.5 | 28.3 | 1.51 | 3.4 | 3.4 | 24.9 | 24.9 | 26.7 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:40:00 | 1.56 | 41.88 | 783205.84 | 755417.6 | 5.03 | 4271.553 | 201.273 | 4.335 | 5 | 175 | 26.4 | 52.5 | 26.6 | 52.1 | 0 | 0 | - | - | 29.6 | 47.4 | 0 | 0 | 0 | 0 | 28.7 | 29.1 | 28.4 | 1.49 | 4.1 | 3.9 | 0 | 27.9 | 28.4 | 28.3 | 1.51 | 3.3 | 3.3 | 24.9 | 24.9 | 26.6 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:45:00 | 1.6 | 42.58 | 783205.88 | 755418.34 | 5.11 | 4271.553 | 201.273 | -9.44 | 5 | 175 | 26.4 | 52.5 | 26.6 | 52.1 | 0 | 0 | - | - | 29.5 | 47.5 | 0 | 0 | 0 | 0 | 28.6 | 28.9 | 28.2 | 1.49 | 4.1 | 3.8 | 0 | 27.8 | 28.4 | 28.3 | 1.51 | 3.3 | 3.2 | 24.9 | 24.9 | 26.6 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:50:00 | 1.6 | 43.28 | 783205.88 | 755419.04 | 5.2 | 4279.009 | 193.818 | -9.652 | 4 | 175 | 26.4 | 52.5 | 26.6 | 52.1 | 0 | 0 | - | - | 29.5 | 47.5 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.2 | 1.49 | 4.1 | 3.7 | 0 | 27.8 | 28.3 | 28.3 | 1.51 | 3.2 | 3.2 | 24.9 | 24.9 | 26.6 | 1.53 | 1.54 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 04:55:00 | 1.6 | 43.94 | 783205.88 | 755419.68 | 5.28 | 4279.009 | 193.818 | -9.196 | 4 | 175 | 26.4 | 52.5 | 26.6 | 52.1 | 0 | 0 | - | - | 29.5 | 47.5 | 0 | 0 | 0 | 0 | 28.4 | 29 | 28.3 | 1.49 | 4 | 3.7 | 0 | 27.8 | 28.4 | 28.3 | 1.51 | 3.3 | 3.1 | 24.9 | 24.9 | 26.7 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:00:00 | 1.6 | 44.64 | 783205.88 | 755420.36 | 5.37 | 4286.464 | 186.363 | -9.744 | 4 | 175 | 26.4 | 52.5 | 26.6 | 52.1 | 0 | 0 | - | - | 29.5 | 47.5 | 0 | 0 | 0 | 0 | 28.4 | 29 | 28.4 | 1.49 | 4 | 3.7 | 0 | 27.8 | 28.4 | 28.4 | 1.51 | 3.3 | 3.2 | 24.9 | 24.9 | 26.8 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:05:00 | 1.6 | 45.44 | 783205.88 | 755421.18 | 5.46 | 4308.826 | 164 | 20.212 | 4 | 175 | 26.4 | 52.5 | 26.6 | 52.1 | 0 | 0 | - | - | 29.6 | 47.5 | 0 | 0 | 0 | 0 | 28.4 | 29 | 28.2 | 1.49 | 4 | 3.7 | 0 | 27.8 | 28.4 | 28.4 | 1.51 | 3.2 | 3.1 | 24.9 | 24.9 | 26.7 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:10:00 | 1.72 | 46.22 | 783206 | 755421.96 | 5.54 | 4308.826 | 164 | -11.117 | 4 | 175 | 26.4 | 52.5 | 26.5 | 52.3 | 0 | 0 | - | - | 29.6 | 47.5 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.2 | 1.49 | 4 | 3.6 | 0 | 27.7 | 28.3 | 28.4 | 1.51 | 3.2 | 3 | 24.9 | 24.9 | 26.8 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:15:00 | 1.72 | 47.04 | 783206 | 755422.76 | 5.63 | 4308.826 | 164 | -8.681 | 4 | 175 | 26.4 | 52.5 | 26.4 | 52.5 | 0 | 0 | - | - | 29.5 | 47.5 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.2 | 1.49 | 4 | 3.7 | 0 | 27.7 | 28.3 | 28.4 | 1.51 | 3.1 | 3 | 25 | 24.9 | 26.8 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:20:00 | 1.8 | 47.8 | 783206.08 | 755423.54 | 5.71 | 4308.826 | 164 | -5.795 | 4 | 175 | 26.4 | 52.5 | 26.5 | 52.3 | 0 | 0 | - | - | 29.5 | 47.6 | 0 | 0 | 0 | 0 | 28.6 | 28.9 | 28.2 | 1.49 | 4 | 3.8 | 0 | 27.8 | 28.3 | 28.3 | 1.51 | 3.1 | 3.1 | 25 | 25 | 26.7 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:25:00 | 1.84 | 48.56 | 783206.12 | 755424.28 | 5.8 | 4308.826 | 164 | -9.629 | 4 | 175 | 26.4 | 52.5 | 26.6 | 52.2 | 0 | 0 | - | - | 29.5 | 47.6 | 0 | 0 | 0 | 0 | 28.5 | 28.8 | 28.2 | 1.49 | 3.9 | 3.7 | 0 | 27.7 | 28.2 | 28.2 | 1.52 | 3 | 3.1 | 25 | 25 | 26.6 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:30:00 | 1.92 | 49.26 | 783206.2 | 755424.98 | 5.88 | 4308.826 | 164 | -11.017 | 4 | 175 | 26.4 | 52.5 | 26.6 | 52.2 | 0 | 0 | - | - | 29.5 | 47.6 | 0 | 0 | 0 | 0 | 28.3 | 28.7 | 27.9 | 1.49 | 3.8 | 3.6 | 0 | 27.7 | 28.2 | 28.2 | 1.51 | 3 | 2.9 | 25 | 25 | 26.4 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:35:00 | 1.96 | 50.04 | 783206.24 | 755425.8 | 5.97 | 4293.918 | 178.908 | -8.991 | 4 | 175 | 26.4 | 52.6 | 26.6 | 52.3 | 0 | 0 | - | - | 29.5 | 47.6 | 0 | 0 | 0 | 0 | 28.2 | 28.6 | 27.9 | 1.49 | 3.6 | 3.4 | 0 | 27.6 | 28.1 | 28.2 | 1.51 | 2.9 | 2.9 | 25 | 25 | 26.4 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:40:00 | 2.02 | 50.76 | 783206.3 | 755426.48 | 6.05 | 4308.826 | 164 | -11.235 | 4 | 175 | 26.4 | 52.6 | 26.5 | 52.4 | 0 | 0 | - | - | 29.5 | 47.7 | 0 | 0 | 0 | 0 | 28.1 | 28.6 | 27.8 | 1.49 | 3.6 | 3.3 | 0 | 27.4 | 28.1 | 28.2 | 1.51 | 2.8 | 2.7 | 25 | 25 | 26.4 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:45:00 | 2.02 | 51.4 | 783206.3 | 755427.14 | 6.13 | 4293.918 | 178.908 | -8.647 | 4 | 175 | 26.4 | 52.6 | 26.6 | 52.3 | 0 | 0 | - | - | 29.5 | 47.7 | 0 | 0 | 0 | 0 | 28.1 | 28.5 | 27.8 | 1.49 | 3.5 | 3.3 | 0 | 27.4 | 28 | 28.1 | 1.51 | 2.8 | 2.7 | 25.1 | 25 | 26.5 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:50:00 | 2.02 | 52.08 | 783206.3 | 755427.82 | 6.22 | 4293.918 | 178.908 | -17.692 | 4 | 175 | 26.4 | 52.6 | 26.6 | 52.3 | 0 | 0 | - | - | 29.5 | 47.7 | 0 | 0 | 0 | 0 | 28 | 28.4 | 27.7 | 1.49 | 3.5 | 3.2 | 0 | 27.4 | 27.9 | 28.1 | 1.52 | 2.7 | 2.6 | 25.1 | 25.1 | 26.5 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 05:55:00 | 2.08 | 52.8 | 783206.36 | 755428.52 | 6.3 | 4308.826 | 164 | 9.594 | 4 | 175 | 26.4 | 52.6 | 26.6 | 52.3 | 0 | 0 | - | - | 29.5 | 47.8 | 0 | 0 | 0 | 0 | 27.9 | 28.4 | 27.7 | 1.49 | 3.4 | 3.1 | 0 | 27.3 | 27.9 | 28.1 | 1.52 | 2.7 | 2.6 | 25.1 | 25.1 | 26.6 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:00:00 | 2.1 | 53.4 | 783206.4 | 755429.12 | 6.38 | 4293.918 | 178.908 | -6.91 | 4 | 175 | 26.4 | 52.7 | 26.7 | 52.3 | 0 | 0 | - | - | 29.5 | 47.8 | 0 | 0 | 0 | 0 | 27.9 | 28.4 | 27.7 | 1.49 | 3.4 | 3.1 | 0 | 27.3 | 27.8 | 28.1 | 1.52 | 2.6 | 2.5 | 25.1 | 25.1 | 26.6 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:05:00 | 3.08 | 53.54 | 783207.38 | 755429.26 | 6.47 | 4293.918 | 178.908 | 15.466 | 4 | 175 | 26.4 | 52.7 | 26.7 | 52.3 | 0 | 0 | - | - | 29.5 | 47.8 | 0 | 0 | 0 | 0 | 28 | 28.4 | 27.8 | 1.49 | 3.5 | 3.3 | 0 | 27.3 | 27.8 | 28.1 | 1.52 | 2.6 | 2.6 | 25.1 | 25.1 | 26.7 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:10:00 | 5.98 | 53.56 | 783210.26 | 755429.28 | 6.55 | 4293.918 | 178.908 | 5.267 | 4 | 175 | 26.4 | 52.7 | 26.7 | 52.3 | 0 | 0 | - | - | 29.5 | 47.8 | 0 | 0 | 0 | 0 | 28.3 | 28.5 | 28 | 1.49 | 3.6 | 3.5 | 0 | 27.5 | 27.9 | 28.1 | 1.52 | 2.7 | 2.7 | 25.1 | 25.1 | 26.7 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:15:00 | 6.04 | 54.32 | 783210.32 | 755430.04 | 6.63 | 4308.826 | 164 | -32.717 | 4 | 175 | 26.4 | 52.7 | 26.7 | 52.3 | 0 | 0 | - | - | 29.5 | 47.8 | 0 | 0 | 0 | 0 | 28.4 | 28.5 | 28.1 | 1.49 | 3.6 | 3.7 | 0 | 27.6 | 28 | 28.1 | 1.52 | 2.8 | 2.8 | 25.1 | 25.1 | 26.8 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:20:00 | 6.1 | 55.12 | 783210.38 | 755430.84 | 6.71 | 4293.918 | 178.908 | -29.622 | 4 | 175 | 26.4 | 52.7 | 26.7 | 52.3 | 0 | 0 | - | - | 29.5 | 47.9 | 0 | 0 | 0 | 0 | 28.6 | 28.6 | 28.3 | 1.49 | 3.6 | 3.8 | 0 | 27.7 | 28.1 | 28.1 | 1.52 | 2.9 | 2.9 | 25.1 | 25.1 | 26.9 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:25:00 | 6.12 | 55.98 | 783210.4 | 755431.76 | 6.8 | 4308.826 | 164 | -10.113 | 4 | 175 | 26.4 | 52.7 | 26.7 | 52.3 | 0 | 0 | - | - | 29.5 | 47.9 | 0 | 0 | 0 | 0 | 28.7 | 28.6 | 28.4 | 1.49 | 3.6 | 3.9 | 0 | 27.8 | 28.2 | 28.1 | 1.52 | 2.9 | 3 | 25.1 | 25.1 | 26.8 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:30:00 | 6.22 | 56.62 | 783210.5 | 755432.38 | 6.88 | 4293.918 | 178.908 | -9.269 | 4 | 175 | 26.5 | 52.7 | 26.7 | 52.3 | 0 | 0 | - | - | 29.5 | 47.8 | 0 | 0 | 0 | 0 | 28.7 | 28.7 | 28.4 | 1.49 | 3.6 | 3.9 | 0 | 27.9 | 28.2 | 28.2 | 1.52 | 2.9 | 3.1 | 25.2 | 25.2 | 26.8 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:35:00 | 6.22 | 57.3 | 783210.5 | 755433.04 | 6.96 | 4293.918 | 178.908 | -10.223 | 4 | 175 | 26.5 | 52.7 | 26.7 | 52.2 | 0 | 0 | - | - | 29.5 | 47.8 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.4 | 1.5 | 3.6 | 4 | 0 | 27.9 | 28.2 | 28.2 | 1.52 | 3 | 3.2 | 25.2 | 25.2 | 27 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:40:00 | 6.3 | 58.1 | 783210.58 | 755433.82 | 7.05 | 4316.281 | 156.546 | -3.362 | 4 | 175 | 26.5 | 52.7 | 26.7 | 52.2 | 0 | 0 | - | - | 29.5 | 47.8 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.4 | 1.5 | 3.6 | 3.9 | 0 | 28 | 28.3 | 28.2 | 1.52 | 3 | 3.2 | 25.2 | 25.2 | 26.9 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:45:00 | 6.32 | 58.9 | 783210.6 | 755434.66 | 7.13 | 4316.281 | 156.546 | -7.698 | 4 | 175 | 26.5 | 52.7 | 26.8 | 52.2 | 0 | 0 | - | - | 29.5 | 47.9 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.5 | 1.5 | 3.6 | 3.9 | 0 | 28 | 28.3 | 28.3 | 1.52 | 3 | 3.2 | 25.2 | 25.2 | 27.3 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:50:00 | 6.44 | 59.62 | 783210.72 | 755435.4 | 7.21 | 4293.918 | 178.908 | -8.494 | 4 | 175 | 26.6 | 52.7 | 26.8 | 52.2 | 0 | 0 | - | - | 29.6 | 47.8 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.8 | 1.5 | 3.7 | 4.1 | 0 | 28.1 | 28.4 | 28.3 | 1.52 | 3.1 | 3.3 | 25.2 | 25.2 | 27.3 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 06:55:00 | 6.44 | 60.36 | 783210.72 | 755436.08 | 7.3 | 4323.734 | 149.092 | -10.081 | 4 | 175 | 26.6 | 52.6 | 26.8 | 52.2 | 0 | 0 | - | - | 29.6 | 47.9 | 0 | 0 | 0 | 0 | 29 | 28.8 | 28.9 | 1.5 | 3.8 | 4.1 | 0 | 28.2 | 28.5 | 28.5 | 1.52 | 3.1 | 3.4 | 25.2 | 25.2 | 27.3 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:00:00 | 6.48 | 61.1 | 783210.76 | 755436.86 | 7.38 | 4323.734 | 149.092 | -10.761 | 4 | 175 | 26.6 | 52.6 | 26.9 | 52.2 | 0 | 0 | - | - | 29.6 | 47.8 | 0 | 0 | 0 | 0 | 29.1 | 28.8 | 28.9 | 1.5 | 3.7 | 4.2 | 0 | 28.3 | 28.5 | 28.6 | 1.52 | 3.2 | 3.4 | 25.2 | 25.2 | 27.5 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:05:00 | 6.56 | 61.68 | 783210.84 | 755437.46 | 7.46 | 4323.734 | 149.092 | -12.546 | 4 | 175 | 26.7 | 52.5 | 26.9 | 52.1 | 0 | 0 | - | - | 29.7 | 47.8 | 0 | 0 | 0 | 0 | 29.2 | 28.8 | 28.9 | 1.5 | 3.7 | 4.3 | 0 | 28.4 | 28.6 | 28.7 | 1.52 | 3.2 | 3.5 | 25.2 | 25.2 | 27.6 | 1.54 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:10:00 | 6.6 | 62.28 | 783210.88 | 755438.04 | 7.54 | 4293.918 | 178.908 | -9.101 | 4 | 175 | 26.7 | 52.5 | 26.9 | 52.1 | 0 | 0 | - | - | 29.7 | 47.8 | 0 | 0 | 0 | 0 | 29.2 | 28.8 | 28.9 | 1.5 | 3.7 | 4.1 | 0 | 28.3 | 28.6 | 28.7 | 1.52 | 3.2 | 3.4 | 25.2 | 25.2 | 27.8 | 1.54 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:15:00 | 6.64 | 63.08 | 783210.92 | 755438.8 | 7.63 | 4293.918 | 178.908 | -12.69 | 4 | 175 | 26.8 | 52.4 | 27 | 52 | 0 | 0 | - | - | 29.8 | 47.7 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 28.8 | 1.5 | 3.7 | 4 | 0 | 28.3 | 28.6 | 28.8 | 1.52 | 3.2 | 3.4 | 25.3 | 25.2 | 27.9 | 1.54 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:20:00 | 6.64 | 63.72 | 783210.92 | 755439.48 | 7.72 | 4323.734 | 149.092 | -10.117 | 4 | 175 | 26.9 | 52.4 | 27 | 52 | 0 | 0 | - | - | 29.8 | 47.7 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 28.8 | 1.5 | 3.8 | 4.1 | 0 | 28.3 | 28.6 | 28.9 | 1.53 | 3.2 | 3.4 | 25.3 | 25.3 | 28 | 1.54 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:25:00 | 6.66 | 66.64 | 783210.96 | 755442.36 | 7.8 | 4323.734 | 149.092 | -3.319 | 4 | 175 | 27 | 52.3 | 27.1 | 52 | 0 | 0 | - | - | 29.9 | 47.6 | 0 | 0 | 0 | 0 | 29.2 | 29 | 28.9 | 1.5 | 3.8 | 4.2 | 0 | 28.4 | 28.7 | 28.9 | 1.53 | 3.2 | 3.5 | 25.3 | 25.3 | 28.1 | 1.54 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:30:00 | 6.82 | 67.06 | 783211.1 | 755442.8 | 7.88 | 4308.826 | 164 | -9.571 | 4 | 175 | 27 | 52.2 | 27.2 | 51.9 | 0 | 0 | - | - | 29.9 | 47.6 | 0 | 0 | 0 | 0 | 29.2 | 29.1 | 28.9 | 1.5 | 3.9 | 4.1 | 0 | 28.4 | 28.7 | 29 | 1.53 | 3.3 | 3.5 | 25.3 | 25.3 | 28.2 | 1.54 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:35:00 | 6.82 | 67.76 | 783211.1 | 755443.5 | 7.96 | 4323.734 | 149.092 | -11.414 | 4 | 175 | 27.1 | 52.1 | 27.2 | 51.9 | 0 | 0 | - | - | 30 | 47.6 | 0 | 0 | 0 | 0 | 29.3 | 29.2 | 29.1 | 1.51 | 3.9 | 4.2 | 0 | 28.5 | 28.8 | 29.1 | 1.53 | 3.3 | 3.5 | 25.3 | 25.3 | 28.3 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:40:00 | 6.82 | 68.6 | 783211.1 | 755444.36 | 8.04 | 4308.826 | 164 | -9.958 | 4 | 175 | 27.2 | 52.1 | 27.3 | 51.8 | 0 | 0 | - | - | 30.1 | 47.5 | 0 | 0 | 0 | 0 | 29.3 | 29.3 | 29.1 | 1.51 | 4 | 4.2 | 0 | 28.6 | 28.9 | 29.2 | 1.53 | 3.3 | 3.5 | 25.3 | 25.3 | 28.6 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:45:00 | 6.84 | 69.3 | 783211.12 | 755445.02 | 8.12 | 4331.188 | 141.638 | -38.268 | 4 | 175 | 27.3 | 51.9 | 27.4 | 51.7 | 0 | 0 | - | - | 30.2 | 47.5 | 0 | 0 | 0 | 0 | 29.5 | 29.4 | 29.3 | 1.51 | 4.1 | 4.3 | 0 | 28.7 | 29 | 29.4 | 1.53 | 3.4 | 3.6 | 25.3 | 25.3 | 28.9 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:50:00 | 6.88 | 70 | 783211.16 | 755445.72 | 8.2 | 4316.281 | 156.546 | -8.246 | 4 | 175 | 27.4 | 51.8 | 27.5 | 51.6 | 0 | 0 | - | - | 30.2 | 47.4 | 0 | 0 | 0 | 0 | 29.6 | 29.6 | 29.5 | 1.51 | 4.2 | 4.4 | 0 | 28.8 | 29.2 | 29.5 | 1.53 | 3.6 | 3.7 | 25.3 | 25.3 | 29 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 07:55:00 | 6.88 | 70.9 | 783211.16 | 755446.62 | 8.29 | 4308.826 | 164 | -10.364 | 4 | 175 | 27.6 | 51.6 | 27.6 | 51.5 | 0 | 0 | - | - | 30.3 | 47.3 | 0 | 0 | 0 | 0 | 29.7 | 29.8 | 29.6 | 1.51 | 4.4 | 4.5 | 0 | 28.9 | 29.2 | 29.6 | 1.53 | 3.6 | 3.8 | 25.4 | 25.4 | 28.8 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:00:00 | 6.88 | 72.46 | 783211.16 | 755448.24 | 8.37 | 4338.642 | 134.184 | -6.129 | 4 | 175 | 27.7 | 51.5 | 27.7 | 51.4 | 0 | 0 | - | - | 30.4 | 47.2 | 0 | 0 | 0 | 0 | 29.9 | 29.9 | 29.6 | 1.51 | 4.5 | 4.6 | 0 | 29 | 29.3 | 29.7 | 1.53 | 3.7 | 3.8 | 25.4 | 25.4 | 29 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:05:00 | 6.92 | 73.4 | 783211.2 | 755449.18 | 8.45 | 4338.642 | 134.184 | -39.739 | 4 | 175 | 27.9 | 51.4 | 27.8 | 51.4 | 0 | 0 | - | - | 30.5 | 47.2 | 0 | 0 | 0 | 0 | 29.9 | 29.9 | 29.7 | 1.51 | 4.5 | 4.7 | 0 | 29.1 | 29.4 | 29.7 | 1.54 | 3.8 | 4 | 25.4 | 25.4 | 29.2 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:10:00 | 6.92 | 74.32 | 783211.2 | 755450.06 | 8.53 | 4338.642 | 134.184 | -14.05 | 4 | 175 | 28 | 51.2 | 27.9 | 51.3 | 0 | 0 | - | - | 30.6 | 47.1 | 0 | 0 | 0 | 0 | 30.1 | 30.1 | 29.8 | 1.52 | 4.6 | 4.8 | 0 | 29.3 | 29.5 | 29.9 | 1.54 | 3.8 | 4.1 | 25.4 | 25.4 | 29.3 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:15:00 | 6.98 | 75.2 | 783211.26 | 755450.92 | 8.61 | 4338.642 | 134.184 | -11.098 | 4 | 175 | 28.1 | 51 | 28 | 51.1 | 0 | 0 | - | - | 30.7 | 47 | 0 | 0 | 0 | 0 | 30.2 | 30.2 | 30.1 | 1.52 | 4.7 | 4.9 | 0 | 29.4 | 29.7 | 30.1 | 1.54 | 4 | 4.2 | 25.4 | 25.4 | 29.5 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:20:00 | 7.04 | 76.02 | 783211.32 | 755451.74 | 8.69 | 4338.642 | 134.184 | -8.698 | 4 | 175 | 28.3 | 50.9 | 28.1 | 51 | 0 | 0 | - | - | 30.9 | 46.9 | 0 | 0 | 0 | 0 | 30.3 | 30.3 | 30.2 | 1.52 | 4.8 | 5 | 0 | 29.5 | 29.7 | 30.3 | 1.54 | 4 | 4.3 | 25.5 | 25.4 | 29.5 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:25:00 | 7.04 | 76.8 | 783211.32 | 755452.54 | 8.77 | 4308.826 | 164 | -9.803 | 4 | 175 | 28.4 | 50.7 | 28.2 | 50.8 | 0 | 0 | - | - | 31 | 46.8 | 0 | 0 | 0 | 0 | 30.4 | 30.4 | 30.2 | 1.51 | 5 | 5.1 | 0 | 29.6 | 29.8 | 30.3 | 1.54 | 4.1 | 4.3 | 25.5 | 25.5 | 29.5 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:30:00 | 7.06 | 77.68 | 783211.34 | 755453.42 | 8.85 | 4338.642 | 134.184 | -10.447 | 4 | 175 | 28.5 | 50.4 | 28.3 | 50.7 | 0 | 0 | - | - | 31 | 46.8 | 0 | 0 | 0 | 0 | 30.5 | 30.4 | 30.3 | 1.52 | 4.9 | 5.2 | 0 | 29.6 | 29.9 | 30.4 | 1.54 | 4.2 | 4.4 | 25.5 | 25.4 | 29.6 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:35:00 | 7.16 | 78.4 | 783211.44 | 755454.14 | 8.93 | 4338.642 | 134.184 | -8.846 | 4 | 175 | 28.7 | 50.4 | 28.5 | 50.6 | 0 | 0 | - | - | 31.2 | 46.7 | 0 | 0 | 0 | 0 | 30.5 | 30.4 | 30.5 | 1.52 | 4.9 | 5.1 | 0 | 29.7 | 30 | 30.5 | 1.54 | 4.2 | 4.4 | 25.5 | 25.5 | 29.7 | 1.56 | 1.57 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:40:00 | 7.16 | 79.16 | 783211.44 | 755454.9 | 9.01 | 4338.642 | 134.184 | -10.157 | 4 | 175 | 28.9 | 50.2 | 28.6 | 50.4 | 0 | 0 | - | - | 31.3 | 46.6 | 0 | 0 | 0 | 0 | 30.6 | 30.5 | 30.7 | 1.52 | 4.9 | 5.1 | 0 | 29.9 | 30.2 | 30.7 | 1.54 | 4.3 | 4.5 | 25.6 | 25.5 | 29.9 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:45:00 | 7.16 | 79.96 | 783211.44 | 755455.68 | 9.1 | 4346.097 | 126.729 | -10.936 | 4 | 175 | 28.9 | 50 | 28.7 | 50.3 | 0 | 0 | - | - | 31.4 | 46.5 | 0 | 0 | 0 | 0 | 30.7 | 30.6 | 30.9 | 1.53 | 4.9 | 5.1 | 0 | 29.9 | 30.3 | 30.9 | 1.54 | 4.4 | 4.6 | 25.6 | 25.6 | 30.3 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:50:00 | 7.2 | 80.66 | 783211.48 | 755456.38 | 9.18 | 4316.281 | 156.546 | -9.756 | 4 | 175 | 29.1 | 49.9 | 28.8 | 50.2 | 0 | 0 | - | - | 31.6 | 46.4 | 0 | 0 | 0 | 0 | 30.8 | 30.8 | 31.2 | 1.53 | 5 | 5.2 | 0 | 30.1 | 30.4 | 31.2 | 1.55 | 4.5 | 4.6 | 25.6 | 25.6 | 30.4 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 08:55:00 | 7.58 | 81.4 | 783211.86 | 755457.12 | 9.26 | 4338.642 | 134.184 | -7.932 | 4 | 175 | 29.3 | 49.7 | 28.9 | 50.1 | 0 | 0 | - | - | 31.7 | 46.3 | 0 | 0 | 0 | 0 | 30.9 | 30.9 | 31.3 | 1.53 | 5.2 | 5.3 | 0 | 30.2 | 30.5 | 31.4 | 1.54 | 4.6 | 4.8 | 25.6 | 25.6 | 30.7 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:00:00 | 7.9 | 82.04 | 783212.2 | 755457.76 | 9.34 | 4316.281 | 156.546 | -3.688 | 4 | 175 | 29.4 | 49.6 | 29 | 50 | 0 | 0 | - | - | 31.9 | 46.2 | 0 | 0 | 0 | 0 | 31.1 | 31 | 31.6 | 1.53 | 5.2 | 5.4 | 0 | 30.3 | 30.6 | 31.7 | 1.55 | 4.7 | 4.9 | 25.6 | 25.6 | 30.8 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:05:00 | 8.28 | 82.64 | 783212.58 | 755458.36 | 9.43 | 4323.736 | 149.091 | 0.819 | 4 | 175 | 29.5 | 49.4 | 29.1 | 49.9 | 0 | 0 | - | - | 32 | 46.1 | 0 | 0 | 0 | 0 | 31.2 | 31.1 | 31.8 | 1.53 | 5.3 | 5.6 | 0 | 30.5 | 30.8 | 31.9 | 1.55 | 4.9 | 5 | 25.7 | 25.6 | 31.1 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:10:00 | 9.02 | 83.16 | 783213.3 | 755458.9 | 9.51 | 4338.642 | 134.184 | 12.93 | 3 | 175 | 29.6 | 49.3 | 29.2 | 49.8 | 0 | 0 | - | - | 32.2 | 46 | 0 | 0 | 0 | 0 | 31.4 | 31.2 | 31.9 | 1.53 | 5.5 | 5.7 | 0 | 30.6 | 31 | 32.1 | 1.55 | 5 | 5.1 | 25.7 | 25.6 | 31.4 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:15:00 | 9.74 | 83.6 | 783214.04 | 755459.32 | 9.59 | 4323.734 | 149.092 | 1.542 | 3 | 175 | 29.8 | 49.2 | 29.3 | 49.7 | 0 | 0 | - | - | 32.3 | 45.9 | 0 | 0 | 0 | 0 | 31.6 | 31.3 | 32.1 | 1.53 | 5.6 | 6 | 0 | 30.8 | 31.1 | 32.3 | 1.55 | 5.1 | 5.3 | 25.7 | 25.7 | 31.5 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:20:00 | 10.46 | 84.2 | 783214.74 | 755459.92 | 9.68 | 4338.642 | 134.184 | 1.609 | 3 | 175 | 29.8 | 49.2 | 29.6 | 49.4 | 0 | 0 | - | - | 32.5 | 45.8 | 0 | 0 | 0 | 0 | 31.7 | 31.4 | 32.3 | 1.53 | 5.7 | 6.1 | 0 | 30.9 | 31.2 | 32.5 | 1.55 | 5.2 | 5.3 | 25.7 | 25.7 | 31.8 | 1.57 | 1.57 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:25:00 | 11.18 | 84.6 | 783215.46 | 755460.32 | 9.76 | 4323.734 | 149.092 | 2.213 | 3 | 175 | 29.8 | 49.2 | 29.9 | 49.1 | 0 | 0 | - | - | 32.6 | 45.7 | 0 | 0 | 0 | 0 | 31.9 | 31.6 | 32.3 | 1.52 | 5.9 | 6.3 | 0 | 31 | 31.3 | 32.6 | 1.55 | 5.3 | 5.5 | 25.7 | 25.7 | 31.5 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:30:00 | 11.9 | 84.96 | 783216.18 | 755460.68 | 9.84 | 4331.188 | 141.638 | 13.963 | 3 | 175 | 30 | 49 | 29.8 | 49.2 | 0 | 0 | - | - | 32.8 | 45.6 | 0 | 0 | 0 | 0 | 32 | 31.6 | 32.4 | 1.52 | 5.9 | 6.5 | 0 | 31.2 | 31.4 | 32.6 | 1.55 | 5.4 | 5.6 | 25.7 | 25.7 | 31.6 | 1.57 | 1.57 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:35:00 | 12.64 | 85.22 | 783216.94 | 755460.98 | 9.93 | 4331.188 | 141.638 | 1.206 | 3 | 175 | 30.2 | 48.7 | 29.8 | 49.3 | 0 | 0 | - | - | 32.9 | 45.5 | 0 | 0 | 0 | 0 | 32.1 | 31.6 | 32.5 | 1.53 | 5.9 | 6.5 | 0 | 31.3 | 31.5 | 32.7 | 1.55 | 5.4 | 5.7 | 25.7 | 25.7 | 31.6 | 1.57 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:40:00 | 13.36 | 85.7 | 783217.66 | 755461.46 | 10.02 | 4331.188 | 141.638 | 1.961 | 3 | 175 | 30.4 | 48.6 | 29.8 | 49.3 | 0 | 0 | - | - | 33 | 45.4 | 0 | 0 | 0 | 0 | 32.3 | 31.7 | 32.7 | 1.53 | 6 | 6.7 | 0 | 31.4 | 31.6 | 32.9 | 1.55 | 5.6 | 5.8 | 25.7 | 25.7 | 31.9 | 1.57 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:45:00 | 14.04 | 86.18 | 783218.32 | 755461.94 | 10.1 | 4338.642 | 134.184 | 0.331 | 4 | 175 | 30.5 | 48.4 | 30 | 49 | 0 | 0 | - | - | 33.2 | 45.4 | 0 | 0 | 0 | 0 | 32.4 | 31.8 | 32.7 | 1.53 | 6.1 | 6.8 | 0 | 31.6 | 31.7 | 33 | 1.55 | 5.6 | 6 | 25.8 | 25.7 | 32.1 | 1.57 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:50:00 | 14.74 | 86.72 | 783219.04 | 755462.44 | 10.19 | 4338.642 | 134.184 | 2.023 | 4 | 175 | 30.6 | 48.3 | 30.2 | 48.8 | 0 | 0 | - | - | 33.3 | 45.3 | 0 | 0 | 0 | 0 | 32.6 | 31.8 | 32.9 | 1.52 | 6.2 | 7 | 0 | 31.7 | 31.8 | 33.2 | 1.55 | 5.8 | 6.1 | 25.8 | 25.7 | 31.9 | 1.56 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 09:55:00 | 15.46 | 87.24 | 783219.74 | 755462.96 | 10.27 | 4338.642 | 134.184 | 1.008 | 4 | 175 | 30.7 | 48.2 | 30.2 | 48.8 | 0 | 0 | - | - | 33.4 | 45.2 | 0 | 0 | 0 | 0 | 32.7 | 31.9 | 33 | 1.52 | 6.2 | 7.2 | 0 | 31.7 | 31.8 | 33.2 | 1.55 | 5.8 | 6.2 | 25.8 | 25.8 | 31.5 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:00:00 | 16.24 | 87.78 | 783220.52 | 755463.5 | 10.36 | 4338.642 | 134.184 | 0.176 | 3 | 175 | 30.8 | 48.1 | 30.2 | 48.9 | 0 | 0 | - | - | 33.5 | 45.2 | 0 | 0 | 0 | 0 | 32.7 | 31.7 | 32.9 | 1.52 | 6 | 7.2 | 0 | 31.8 | 31.7 | 33.1 | 1.55 | 5.8 | 6.3 | 25.8 | 25.8 | 31.7 | 1.57 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:05:00 | 16.9 | 88.34 | 783221.2 | 755464.06 | 10.45 | 4338.642 | 134.184 | 0.773 | 3 | 175 | 30.9 | 48 | 30.2 | 48.9 | 0 | 0 | - | - | 33.6 | 45.1 | 0 | 0 | 0 | 0 | 32.8 | 31.7 | 33.1 | 1.52 | 6 | 7.3 | 0 | 31.9 | 31.8 | 33.2 | 1.55 | 5.8 | 6.4 | 25.8 | 25.8 | 31.9 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:10:00 | 17.78 | 88.76 | 783222.12 | 755464.48 | 10.54 | 4338.642 | 134.184 | 9.15 | 3 | 175 | 31 | 47.9 | 30.3 | 48.8 | 0 | 0 | - | - | 33.7 | 45 | 0 | 0 | 0 | 0 | 32.9 | 31.7 | 33.2 | 1.53 | 6 | 7.3 | 0 | 32.1 | 31.9 | 33.3 | 1.55 | 5.9 | 6.5 | 25.8 | 25.8 | 32 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:15:00 | 18.84 | 89.2 | 783223.14 | 755464.92 | 10.63 | 4338.642 | 134.184 | 5.978 | 3 | 175 | 31.1 | 47.9 | 30.3 | 48.8 | 0 | 0 | - | - | 33.8 | 45 | 0 | 0 | 0 | 0 | 33 | 31.8 | 33.3 | 1.53 | 6 | 7.4 | 0 | 32.2 | 31.9 | 33.4 | 1.55 | 5.9 | 6.7 | 25.9 | 25.8 | 32.4 | 1.57 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:20:00 | 19.58 | 89.7 | 783223.88 | 755465.44 | 10.72 | 4331.188 | 141.638 | -21.738 | 3 | 175 | 31.2 | 47.8 | 30.4 | 48.7 | 0 | 0 | - | - | 34 | 44.9 | 0 | 0 | 0 | 0 | 33.1 | 31.9 | 33.4 | 1.53 | 6.1 | 7.5 | 0 | 32.2 | 31.9 | 33.6 | 1.55 | 6 | 6.8 | 25.9 | 25.8 | 32.7 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:25:00 | 20.32 | 90.34 | 783224.62 | 755466.06 | 10.8 | 4338.642 | 134.184 | 0.314 | 3 | 175 | 31.3 | 47.7 | 30.5 | 48.7 | 0 | 0 | - | - | 34.1 | 44.8 | 0 | 0 | 0 | 0 | 33.3 | 32.1 | 33.6 | 1.53 | 6.3 | 7.7 | 0 | 32.4 | 32 | 33.7 | 1.55 | 6 | 7 | 25.9 | 25.9 | 32.9 | 1.57 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:30:00 | 20.84 | 91.06 | 783225.14 | 755466.78 | 10.89 | 4338.642 | 134.184 | -4.985 | 3 | 175 | 31.4 | 47.6 | 30.6 | 48.6 | 0 | 0 | - | - | 34.2 | 44.8 | 0 | 0 | 0 | 0 | 33.4 | 32.1 | 33.6 | 1.53 | 6.3 | 7.7 | 0 | 32.5 | 32.1 | 33.8 | 1.55 | 6.1 | 7 | 25.9 | 25.9 | 32.6 | 1.57 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:35:00 | 21.24 | 91.84 | 783225.52 | 755467.58 | 10.98 | 4338.642 | 134.184 | -4.586 | 3 | 175 | 31.5 | 47.6 | 30.7 | 48.5 | 0 | 0 | - | - | 34.4 | 44.7 | 0 | 0 | 0 | 0 | 33.4 | 32.1 | 33.7 | 1.53 | 6.3 | 7.7 | 0 | 32.6 | 32.1 | 33.9 | 1.55 | 6 | 7.1 | 25.9 | 25.9 | 32.8 | 1.57 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:40:00 | 21.64 | 92.44 | 783225.92 | 755468.18 | 11.06 | 4323.734 | 149.092 | -5.605 | 3 | 175 | 31.5 | 47.5 | 30.8 | 48.4 | 0 | 0 | - | - | 34.5 | 44.6 | 0 | 0 | 0 | 0 | 33.6 | 32.3 | 33.8 | 1.53 | 6.4 | 7.9 | 0 | 32.7 | 32.2 | 34 | 1.55 | 6.2 | 7.2 | 26 | 25.9 | 32.6 | 1.57 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:45:00 | 22.18 | 93.22 | 783226.46 | 755468.96 | 11.16 | 4338.642 | 134.184 | -14.213 | 4 | 175 | 31.7 | 47.4 | 30.8 | 48.4 | 0 | 0 | - | - | 34.6 | 44.5 | 0 | 0 | 0 | 0 | 33.6 | 32.2 | 33.8 | 1.53 | 6.4 | 7.9 | 0 | 32.7 | 32.1 | 34 | 1.55 | 6.1 | 7.2 | 26 | 25.9 | 32.9 | 1.57 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:50:00 | 22.66 | 93.96 | 783226.96 | 755469.68 | 11.25 | 4338.642 | 134.184 | -1.931 | 4 | 175 | 31.7 | 47.3 | 30.8 | 48.3 | 0 | 0 | - | - | 34.8 | 44.4 | 0 | 0 | 0 | 0 | 33.7 | 32.4 | 33.9 | 1.53 | 6.6 | 8 | 0 | 32.8 | 32.2 | 34.1 | 1.55 | 6.1 | 7.3 | 26 | 26 | 32.8 | 1.57 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 10:55:00 | 23.36 | 94.58 | 783227.66 | 755470.3 | 11.33 | 4338.642 | 134.184 | 13.68 | 4 | 175 | 31.7 | 47.2 | 30.9 | 48.3 | 0 | 0 | - | - | 34.9 | 44.4 | 0 | 0 | 0 | 0 | 33.7 | 32.4 | 34 | 1.53 | 6.5 | 8 | 0 | 32.9 | 32.1 | 34.1 | 1.55 | 6.1 | 7.4 | 26.1 | 26 | 33.2 | 1.57 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:00:00 | 38.42 | 94.68 | 783243.24 | 755470.4 | 11.43 | 4331.188 | 141.638 | 383.857 | 4 | 175 | 31.9 | 47.2 | 31.1 | 48.2 | 0 | 0 | - | - | 35 | 44.2 | 0 | 0 | 0 | 0 | 33.9 | 32.4 | 34.1 | 1.53 | 6.5 | 8.2 | 0 | 33 | 32.1 | 34.3 | 1.55 | 6.1 | 7.4 | 26.1 | 26 | 33.6 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:05:00 | 95.88 | 94.68 | 783302.2 | 755470.4 | 11.53 | 4264.098 | 208.728 | 970.568 | 5 | 175 | 32 | 47.1 | 31.2 | 48.1 | 0 | 0 | - | - | 35.2 | 44.2 | 0 | 0 | 0 | 0 | 34.1 | 32.6 | 34.3 | 1.53 | 6.7 | 8.3 | 0 | 33.1 | 32.2 | 34.4 | 1.55 | 6.1 | 7.5 | 26 | 26 | 33.7 | 1.57 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:10:00 | 183.66 | 94.68 | 783390.26 | 755470.4 | 11.65 | 4197.003 | 275.823 | 1165.331 | 7 | 175 | 32.1 | 47 | 31.4 | 48 | 0 | 0 | - | - | 35.3 | 44.1 | 0 | 0 | 0 | 0 | 34.1 | 32.7 | 34.4 | 1.53 | 6.8 | 8.4 | 0 | 33.3 | 32.3 | 34.6 | 1.55 | 6.3 | 7.8 | 26 | 25.8 | 33.9 | 1.57 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:15:00 | 277 | 94.68 | 783483.76 | 755470.4 | 11.77 | 4107.549 | 365.277 | 1167.032 | 9 | 175 | 32.3 | 46.8 | 31.5 | 47.8 | 0 | 0 | - | - | 35.4 | 44 | 0 | 0 | 0 | 0 | 34.1 | 32.7 | 34.4 | 1.53 | 6.9 | 8.4 | 0 | 33.3 | 32.4 | 34.7 | 1.55 | 6.3 | 7.7 | 26 | 25.9 | 33.5 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:20:00 | 374.84 | 94.68 | 783581.6 | 755470.4 | 11.9 | 4010.636 | 462.19 | 1173.108 | 12 | 175 | 32.5 | 46.7 | 31.7 | 47.7 | 0 | 0 | - | - | 35.6 | 43.9 | 0 | 0 | 0 | 0 | 34.2 | 32.7 | 34.4 | 1.53 | 6.8 | 8.5 | 0 | 33.4 | 32.4 | 34.7 | 1.55 | 6.3 | 7.7 | 26.2 | 26.1 | 33.1 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:25:00 | 474.08 | 94.68 | 783679.02 | 755470.4 | 12.04 | 3921.18 | 551.646 | 1176.22 | 14 | 175 | 32.6 | 46.7 | 31.8 | 47.7 | 0 | 0 | - | - | 35.7 | 43.8 | 0 | 0 | 0 | 0 | 34.2 | 32.6 | 34.4 | 1.54 | 6.6 | 8.3 | 0 | 33.4 | 32.4 | 34.8 | 1.56 | 6.1 | 7.8 | 26.3 | 26.2 | 32.9 | 1.58 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:30:00 | 570.7 | 94.68 | 783776.82 | 755470.4 | 12.19 | 3831.722 | 641.104 | 1368.232 | 16 | 175 | 32.7 | 46.6 | 31.9 | 47.6 | 0 | 0 | - | - | 35.8 | 43.8 | 0 | 0 | 0 | 0 | 34.2 | 32.6 | 34.5 | 1.55 | 6.3 | 8.2 | 0 | 33.5 | 32.3 | 34.9 | 1.56 | 5.9 | 7.7 | 26.5 | 26.5 | 32.9 | 1.59 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:35:00 | 697.84 | 94.68 | 783904.22 | 755470.4 | 12.34 | 3697.539 | 775.287 | 1956.29 | 19 | 175 | 32.8 | 46.5 | 32 | 47.6 | 0 | 0 | - | - | 35.9 | 43.7 | 0 | 0 | 0 | 0 | 34.3 | 32.5 | 34.6 | 1.55 | 6.1 | 8.2 | 0 | 33.6 | 32.2 | 35 | 1.57 | 5.7 | 7.6 | 26.7 | 26.7 | 33.4 | 1.59 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:40:00 | 859.8 | 94.68 | 784068.16 | 755470.4 | 12.84 | 3555.897 | 916.929 | 1957.516 | 23 | 175 | 33 | 46.4 | 32.2 | 47.5 | 0 | 0 | - | - | 36 | 43.7 | 223 | 220 | 57 | 56.8 | 62.1 | 26.3 | 42.5 | 2.49 | 11.9 | 17.5 | 56.7 | 62.6 | 26.3 | 44.1 | 2.63 | 12.6 | 16.3 | 23.1 | 25.3 | 33.4 | 2.59 | 1.11 | 2.77 | 1.14 | 223 | 216 | 2667 | 2680
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:45:00 | 1025.22 | 94.68 | 784231.62 | 755470.4 | 13.67 | 3391.894 | 1080.932 | 2014.211 | 26 | 175 | 33.4 | 46 | 32.3 | 47.3 | 0 | 0 | - | - | 36.2 | 43.7 | 222 | 216 | 63 | 63.2 | 71.2 | 23.7 | 43.9 | 2.51 | 11.2 | 26.2 | 63.1 | 74.3 | 23.7 | 47.1 | 2.74 | 9.9 | 26.3 | 21.7 | 23.6 | 34.1 | 2.55 | 1.07 | 2.78 | 1.11 | 222 | 216 | 2563 | 2575
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:50:00 | 1195.58 | 94.68 | 784401.88 | 755470.4 | 14.42 | 3227.89 | 1244.936 | 2027.572 | 30 | 175 | 33.7 | 45.6 | 32.4 | 47.1 | 0 | 0 | - | - | 36.3 | 43.5 | 222 | 216 | 60.9 | 61.1 | 70.6 | 23.3 | 43.7 | 2.51 | 10.2 | 25.5 | 60.8 | 73.7 | 23.3 | 46.4 | 2.7 | 9.2 | 26.3 | 21.6 | 23.3 | 34.4 | 2.51 | 1.09 | 2.72 | 1.13 | 222 | 216 | 2271 | 2271
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 11:55:00 | 1357.12 | 94.68 | 784566.38 | 755470.4 | 15.14 | 3063.886 | 1408.94 | 1963.53 | 34 | 175 | 34 | 45.3 | 32.6 | 47 | 0 | 0 | - | - | 36.6 | 43.4 | 222 | 216 | 60.5 | 60.4 | 70.3 | 23.4 | 43.1 | 2.46 | 10.2 | 26.1 | 60.5 | 73.3 | 23.4 | 46.4 | 2.69 | 9.1 | 26.1 | 21.8 | 23.5 | 35.6 | 2.51 | 1.09 | 2.72 | 1.13 | 222 | 216 | 2265 | 2265
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:00:00 | 1521.38 | 94.68 | 784728.86 | 755470.4 | 15.83 | 2914.792 | 1558.034 | 1967.562 | 37 | 175 | 34.4 | 45 | 32.8 | 46.7 | 0 | 0 | - | - | 36.8 | 43.3 | 222 | 216 | 59.4 | 59.3 | 69.1 | 23.6 | 42.5 | 2.45 | 10.5 | 25.1 | 59.4 | 72.6 | 23.6 | 45.9 | 2.68 | 9.2 | 25.6 | 21.9 | 23.6 | 35 | 2.55 | 1.09 | 2.74 | 1.13 | 222 | 216 | 2265 | 2265
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:05:00 | 1690.52 | 94.68 | 784894.8 | 755470.4 | 16.54 | 2750.788 | 1722.038 | 2044.316 | 41 | 175 | 34.7 | 44.8 | 33.1 | 46.5 | 0 | 0 | - | - | 37 | 43.2 | 222 | 216 | 59.7 | 59.8 | 70 | 23.9 | 42.9 | 2.41 | 10.2 | 26.7 | 59.7 | 73.4 | 23.9 | 46.4 | 2.68 | 9.2 | 26.3 | 22.2 | 23.9 | 34.6 | 2.52 | 1.1 | 2.73 | 1.14 | 222 | 216 | 2265 | 2265
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:10:00 | 1853.22 | 94.68 | 785059.34 | 755470.4 | 17.25 | 2579.33 | 1893.496 | 1807.057 | 45 | 175 | 35.1 | 44.5 | 33.3 | 46.3 | 0 | 0 | - | - | 37.2 | 43 | 222 | 216 | 59.2 | 59.3 | 69.1 | 24.1 | 42.5 | 2.44 | 10.3 | 25.2 | 59.6 | 72.8 | 24.1 | 46.2 | 2.69 | 9.3 | 25.7 | 22.6 | 24.2 | 34.6 | 2.54 | 1.11 | 2.75 | 1.15 | 222 | 216 | 2265 | 2265
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:15:00 | 2003.52 | 94.68 | 785209.46 | 755470.4 | 17.96 | 2437.69 | 2035.136 | 1613.612 | 48 | 175 | 35.4 | 44.1 | 33.6 | 46.2 | 0 | 0 | - | - | 37.5 | 42.9 | 222 | 216 | 59.9 | 59.7 | 69.1 | 24.5 | 42.7 | 2.46 | 10.4 | 24.9 | 59.6 | 72.7 | 24.5 | 46.2 | 2.7 | 9.2 | 25.4 | 22.9 | 24.6 | 34.6 | 2.59 | 1.11 | 2.78 | 1.16 | 222 | 216 | 2265 | 2265
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:20:00 | 2139.2 | 94.68 | 785345.14 | 755470.4 | 18.67 | 2303.506 | 2169.32 | 1618.333 | 51 | 175 | 36 | 43.8 | 33.8 | 46 | 0 | 0 | - | - | 37.7 | 42.8 | 222 | 216 | 59.9 | 60.2 | 69.5 | 24.8 | 42.9 | 2.45 | 10.4 | 25.5 | 60.2 | 73 | 24.9 | 46.5 | 2.71 | 9.3 | 25.7 | 23.2 | 25 | 34.6 | 2.58 | 1.13 | 2.77 | 1.17 | 222 | 216 | 2272 | 2272
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:25:00 | 2280.52 | 94.68 | 785486.62 | 755470.4 | 19.41 | 2161.867 | 2310.959 | 1706.6 | 54 | 175 | 36.5 | 43.5 | 34.1 | 46 | 0 | 0 | - | - | 38 | 42.6 | 222 | 216 | 61.6 | 61.4 | 70.1 | 25.2 | 43.6 | 2.52 | 10.7 | 25 | 61.7 | 73.5 | 25.2 | 46.9 | 2.75 | 9.6 | 25.3 | 23.5 | 25.3 | 34.6 | 2.57 | 1.13 | 2.78 | 1.17 | 222 | 216 | 2320 | 2320
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:30:00 | 2414.58 | 94.68 | 785620.6 | 755470.4 | 20.14 | 2035.137 | 2437.689 | 1627.785 | 57 | 175 | 36.6 | 43.4 | 34.3 | 45.9 | 0 | 0 | - | - | 38.2 | 42.4 | 222 | 216 | 60.6 | 60.9 | 70 | 25.4 | 43.5 | 2.5 | 10.7 | 25.2 | 60.6 | 73.7 | 25.4 | 46.8 | 2.74 | 9.7 | 25.8 | 23.7 | 25.5 | 34.6 | 2.6 | 1.13 | 2.81 | 1.17 | 222 | 216 | 2338 | 2338
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:35:00 | 2537.08 | 94.68 | 785742.64 | 755470.4 | 20.91 | 1900.949 | 2571.877 | 1224.295 | 59 | 175 | 36.8 | 43.4 | 34.6 | 45.7 | 0 | 0 | - | - | 38.5 | 42.3 | 222 | 216 | 63.7 | 63.4 | 71.6 | 25.7 | 44.3 | 2.57 | 11.3 | 25.7 | 63.4 | 75 | 25.7 | 47.7 | 2.81 | 10.1 | 26.1 | 24 | 25.9 | 36 | 2.65 | 1.14 | 2.86 | 1.18 | 222 | 216 | 2395 | 2395
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:40:00 | 2640.28 | 94.68 | 785846.54 | 755470.4 | 21.72 | 1811.494 | 2661.332 | 1238.132 | 62 | 175 | 37 | 43.3 | 34.8 | 45.6 | 0 | 0 | - | - | 38.8 | 42.1 | 222 | 216 | 64.9 | 65.3 | 72.9 | 25.9 | 44.7 | 2.55 | 11.3 | 27.3 | 65.5 | 76.2 | 26 | 48.3 | 2.83 | 10.1 | 27 | 24.2 | 26 | 35.4 | 2.61 | 1.14 | 2.86 | 1.18 | 222 | 216 | 2488 | 2488
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:45:00 | 2743.06 | 94.68 | 785949.32 | 755470.4 | 22.53 | 1707.129 | 2765.697 | 1242.876 | 64 | 175 | 37.2 | 43.2 | 35 | 45.5 | 0 | 0 | - | - | 39 | 42 | 223 | 216 | 63.9 | 63.7 | 71.7 | 26.1 | 43.9 | 2.53 | 11.2 | 26.4 | 64 | 75.9 | 26.1 | 47.9 | 2.81 | 10 | 27 | 24.2 | 26.1 | 35 | 2.67 | 1.14 | 2.87 | 1.18 | 223 | 216 | 2497 | 2497
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:50:00 | 2841.9 | 94.68 | 786046.76 | 755470.4 | 23.35 | 1587.851 | 2884.975 | 1032.385 | 66 | 175 | 37.4 | 43.1 | 35.1 | 45.5 | 0 | 0 | - | - | 39.2 | 41.9 | 223 | 216 | 62.9 | 62.9 | 71.5 | 26.2 | 44.1 | 2.52 | 10.9 | 26.3 | 63 | 75.7 | 26.2 | 47.7 | 2.79 | 10 | 27 | 24.3 | 26.2 | 34.6 | 2.65 | 1.15 | 2.87 | 1.19 | 223 | 216 | 2497 | 2497
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 12:55:00 | 2900.82 | 94.68 | 786105.4 | 755470.4 | 24.17 | 1543.125 | 2929.701 | 183.973 | 67 | 175 | 37.6 | 43 | 35.3 | 45.5 | 0 | 0 | - | - | 39.4 | 41.8 | 223 | 216 | 65.1 | 65.1 | 72.5 | 26.3 | 44.7 | 2.58 | 11.3 | 26.3 | 64.9 | 76.1 | 26.4 | 48.2 | 2.83 | 10.2 | 26.7 | 24.4 | 26.3 | 35.2 | 2.64 | 1.15 | 2.89 | 1.18 | 223 | 216 | 2544 | 2550
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:00:00 | 2913.08 | 95 | 786117.36 | 755470.74 | 25 | 1543.125 | 2929.701 | -14.344 | 68 | 175 | 37.7 | 43 | 35.3 | 45.5 | 0 | 0 | - | - | 39.5 | 41.7 | 224 | 216 | 63.8 | 64 | 72.4 | 26.3 | 44.4 | 2.57 | 11.3 | 26.4 | 63.8 | 75.9 | 26.2 | 48.1 | 2.82 | 10.1 | 26.7 | 24.2 | 26.2 | 34.9 | 2.67 | 1.15 | 2.88 | 1.19 | 224 | 216 | 2622 | 2631
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:05:00 | 2917.04 | 96.3 | 786121.52 | 755472.02 | 25.85 | 1543.125 | 2929.701 | 185.666 | 68 | 175 | 37.8 | 42.9 | 35.3 | 45.6 | 0 | 0 | - | - | 39.6 | 41.7 | 224 | 216 | 62.7 | 63 | 71.2 | 25.9 | 43.9 | 2.51 | 11 | 26.1 | 63.1 | 75.2 | 25.9 | 47.6 | 2.78 | 9.7 | 26.7 | 24 | 26 | 33.4 | 2.6 | 1.15 | 2.84 | 1.19 | 224 | 216 | 2635 | 2635
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:10:00 | 2959.38 | 96.3 | 786164.64 | 755472.02 | 26.68 | 1498.396 | 2974.43 | 636.416 | 69 | 175 | 37.6 | 43 | 35.2 | 45.6 | 0 | 0 | - | - | 39.6 | 41.7 | 224 | 216 | 63.2 | 63.1 | 71.2 | 25.7 | 43.9 | 2.51 | 11 | 26 | 62.9 | 74.7 | 25.7 | 47.4 | 2.78 | 9.7 | 26.2 | 23.8 | 25.7 | 33.8 | 2.65 | 1.13 | 2.86 | 1.17 | 224 | 216 | 2635 | 2635
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:15:00 | 3017.76 | 96.3 | 786222.88 | 755472.02 | 27.54 | 1423.849 | 3048.977 | 830.988 | 70 | 175 | 37.4 | 43.2 | 35.1 | 45.8 | 0 | 0 | - | - | 39.5 | 41.8 | 224 | 216 | 64 | 63.7 | 71.6 | 25.6 | 44.2 | 2.55 | 11 | 25.9 | 64.1 | 75.5 | 25.6 | 47.7 | 2.8 | 9.9 | 26.6 | 23.7 | 25.7 | 33.9 | 2.62 | 1.14 | 2.84 | 1.18 | 224 | 216 | 2635 | 2635
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:20:00 | 3087.1 | 96.3 | 786293.6 | 755472.02 | 28.4 | 1364.211 | 3108.615 | 836.926 | 72 | 175 | 37.2 | 43.4 | 35 | 45.9 | 0 | 0 | - | - | 39.4 | 41.9 | 224 | 216 | 64.5 | 64.4 | 72.7 | 25.6 | 44.9 | 2.6 | 10.9 | 26.2 | 64.6 | 76.2 | 25.5 | 48.1 | 2.81 | 10.1 | 27.2 | 23.7 | 25.6 | 34.2 | 2.69 | 1.14 | 2.84 | 1.16 | 224 | 216 | 2635 | 2635
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:25:00 | 3157.5 | 96.3 | 786363.94 | 755472.02 | 29.24 | 1274.753 | 3198.073 | 839.591 | 73 | 175 | 37.2 | 43.5 | 34.9 | 46 | 0 | 0 | - | - | 39.3 | 41.9 | 224 | 216 | 60.9 | 60.8 | 71 | 25.3 | 44 | 2.54 | 10.3 | 25.5 | 60.5 | 74.9 | 25.4 | 46.9 | 2.73 | 9.9 | 26.9 | 23.4 | 25.4 | 32.1 | 2.64 | 1.15 | 2.8 | 1.16 | 224 | 216 | 2635 | 2635
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:30:00 | 3241.24 | 96.3 | 786446.62 | 755472.02 | 30.13 | 1192.752 | 3280.074 | 1039.653 | 75 | 175 | 36.7 | 43.9 | 34.8 | 46 | 0 | 0 | - | - | 39.2 | 42 | 224 | 216 | 60.3 | 60.4 | 70.6 | 25.2 | 44.1 | 2.53 | 10.3 | 25.3 | 60.4 | 74.4 | 25.2 | 46.8 | 2.73 | 10 | 26.6 | 23.2 | 25.3 | 31.9 | 2.64 | 1.14 | 2.79 | 1.16 | 224 | 216 | 2635 | 2635
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:35:00 | 3332.96 | 96.3 | 786539.2 | 755472.02 | 30.95 | 1088.388 | 3384.441 | 1259.866 | 77 | 175 | 36.2 | 44.3 | 34.7 | 46.1 | 0 | 0 | - | - | 39 | 42.2 | 224 | 216 | 59.6 | 59.6 | 70.4 | 25.1 | 43.6 | 2.5 | 10.2 | 25.4 | 59.7 | 74.3 | 25.1 | 46.4 | 2.71 | 9.9 | 26.8 | 23.1 | 25.2 | 31.4 | 2.59 | 1.14 | 2.78 | 1.15 | 224 | 216 | 2635 | 2635
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:40:00 | 3438.28 | 96.3 | 786645.18 | 755472.02 | 31.79 | 976.564 | 3496.262 | 1266.645 | 79 | 175 | 36 | 44.6 | 34.5 | 46.4 | 0 | 0 | - | - | 38.8 | 42.3 | 224 | 216 | 59.8 | 59.7 | 70.1 | 24.9 | 43.5 | 2.5 | 10.3 | 25.2 | 59.7 | 74.1 | 25.1 | 46.4 | 2.71 | 9.8 | 26.5 | 23 | 25.1 | 31.3 | 2.6 | 1.14 | 2.77 | 1.15 | 224 | 216 | 2629 | 2634
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:45:00 | 3544.34 | 96.3 | 786750.56 | 755472.02 | 32.61 | 879.654 | 3593.172 | 1266.374 | 82 | 175 | 35.7 | 44.8 | 34.2 | 46.6 | 0 | 0 | - | - | 38.5 | 42.5 | 224 | 216 | 60.3 | 60.7 | 70.2 | 24.8 | 43.6 | 2.5 | 10.2 | 25.3 | 60.2 | 74.2 | 24.9 | 46.6 | 2.72 | 9.9 | 26.4 | 22.9 | 25 | 31.3 | 2.59 | 1.13 | 2.77 | 1.15 | 224 | 216 | 2628 | 2628
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:50:00 | 3640.36 | 96.3 | 786845.08 | 755472.02 | 33.44 | 790.195 | 3682.631 | 845.444 | 84 | 175 | 35.5 | 45 | 34 | 46.8 | 0 | 0 | - | - | 38.3 | 42.7 | 224 | 216 | 61.9 | 62.2 | 70.9 | 24.8 | 44 | 2.54 | 10.5 | 25.4 | 62.2 | 74.6 | 24.9 | 46.9 | 2.76 | 10 | 26.3 | 23 | 24.9 | 33 | 2.64 | 1.12 | 2.82 | 1.14 | 224 | 216 | 2625 | 2625
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 13:55:00 | 3671.12 | 96.48 | 786875.4 | 755472.26 | 34.27 | 745.47 | 3727.356 | -15.128 | 84 | 175 | 35.1 | 45.3 | 33.8 | 47 | 0 | 0 | - | - | 38.1 | 42.9 | 224 | 216 | 62.5 | 62.7 | 71.2 | 24.9 | 43.6 | 2.5 | 10.7 | 26.3 | 62.7 | 75.3 | 24.9 | 47.2 | 2.76 | 10 | 27 | 22.9 | 24.9 | 33.8 | 2.58 | 1.12 | 2.8 | 1.15 | 224 | 216 | 2625 | 2625
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:00:00 | 3671.12 | 97.56 | 786875.4 | 755473.32 | 35.07 | 745.47 | 3727.356 | -13.046 | 84 | 175 | 34.8 | 45.6 | 33.6 | 47.2 | 0 | 0 | - | - | 37.9 | 43.1 | 224 | 216 | 61 | 60.7 | 69.6 | 24.8 | 42.4 | 2.44 | 10.5 | 25.8 | 60.6 | 74.5 | 24.7 | 46.6 | 2.72 | 9.8 | 26.8 | 22.7 | 24.7 | 33 | 2.53 | 1.12 | 2.77 | 1.14 | 224 | 216 | 2625 | 2625
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:05:00 | 3685.42 | 97.78 | 786890.14 | 755473.5 | 35.86 | 738.015 | 3734.811 | 209.052 | 85 | 175 | 34.5 | 45.9 | 33.3 | 47.5 | 0 | 0 | - | - | 37.6 | 43.3 | 224 | 216 | 60 | 59.7 | 68.7 | 24.6 | 41.9 | 2.4 | 10.5 | 25.4 | 59.6 | 73.7 | 24.6 | 46.1 | 2.69 | 9.7 | 26.5 | 22.6 | 24.6 | 31.9 | 2.48 | 1.11 | 2.73 | 1.14 | 224 | 216 | 2625 | 2625
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:10:00 | 3702.66 | 97.78 | 786907.28 | 755473.5 | 36.61 | 715.65 | 3757.176 | 217.246 | 85 | 175 | 34.5 | 45.9 | 33 | 47.7 | 0 | 0 | - | - | 37.4 | 43.4 | 224 | 216 | 58.9 | 58.6 | 67.9 | 24.3 | 41.6 | 2.38 | 10.5 | 25 | 59.1 | 73.1 | 24.3 | 45.9 | 2.67 | 9.6 | 26.3 | 22.3 | 24.3 | 31.2 | 2.48 | 1.11 | 2.72 | 1.14 | 224 | 216 | 2625 | 2625
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:15:00 | 3721.06 | 97.78 | 786926.18 | 755473.5 | 37.4 | 700.741 | 3772.085 | 419.025 | 85 | 175 | 34.2 | 46 | 32.7 | 47.9 | 0 | 0 | - | - | 37 | 43.7 | 224 | 216 | 58.9 | 59.1 | 68 | 24.1 | 41.6 | 2.39 | 10.4 | 24.8 | 59.1 | 72.9 | 24.1 | 45.7 | 2.67 | 9.6 | 26 | 22.2 | 24.1 | 31.4 | 2.5 | 1.1 | 2.73 | 1.13 | 224 | 216 | 2625 | 2625
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:20:00 | 3756.68 | 97.78 | 786960.96 | 755473.5 | 38.2 | 663.466 | 3809.36 | 431.256 | 86 | 175 | 34 | 46.1 | 32.4 | 48.2 | 0 | 0 | - | - | 36.7 | 43.9 | 224 | 216 | 59.4 | 59.5 | 68.5 | 23.8 | 41.7 | 2.39 | 10.5 | 25.3 | 59.1 | 73.3 | 23.8 | 45.7 | 2.66 | 9.6 | 26.5 | 21.9 | 23.8 | 31.8 | 2.47 | 1.09 | 2.71 | 1.12 | 224 | 216 | 2625 | 2625
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:25:00 | 3791.28 | 97.78 | 786995.56 | 755473.5 | 38.99 | 618.741 | 3854.085 | 428.535 | 87 | 175 | 33.7 | 46.3 | 32 | 48.5 | 0 | 0 | - | - | 36.5 | 44.1 | 224 | 216 | 57.4 | 57.5 | 67.5 | 23.7 | 40.9 | 2.35 | 10.2 | 25 | 57.5 | 72.5 | 23.7 | 45.1 | 2.62 | 9.4 | 26.3 | 21.7 | 23.7 | 30.3 | 2.43 | 1.09 | 2.66 | 1.12 | 224 | 216 | 2574 | 2568
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:30:00 | 3826.6 | 97.78 | 787031.54 | 755473.5 | 39.71 | 581.466 | 3891.36 | 411.694 | 88 | 175 | 33.3 | 46.6 | 31.6 | 48.9 | 0 | 0 | - | - | 36.2 | 44.3 | 224 | 216 | 54.3 | 54.3 | 66 | 23.4 | 40.1 | 2.3 | 9.9 | 24.4 | 54.4 | 70.7 | 23.5 | 44.1 | 2.56 | 9.1 | 25.5 | 21.6 | 23.6 | 29.6 | 2.38 | 1.1 | 2.6 | 1.13 | 224 | 216 | 2407 | 2410
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:35:00 | 3871.84 | 97.78 | 787077.08 | 755473.5 | 40.4 | 529.281 | 3943.546 | 633.281 | 89 | 175 | 32.8 | 47 | 31.1 | 49.3 | 0 | 0 | - | - | 35.9 | 44.6 | 224 | 216 | 53.3 | 53.3 | 65 | 23.4 | 39.6 | 2.28 | 10 | 23.8 | 53.3 | 69.5 | 23.4 | 43.6 | 2.53 | 9.1 | 24.8 | 21.6 | 23.5 | 29.1 | 2.37 | 1.09 | 2.59 | 1.12 | 224 | 216 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:40:00 | 3926.4 | 97.78 | 787132.4 | 755473.5 | 41.09 | 484.552 | 3988.274 | 657.125 | 90 | 175 | 32.4 | 47.4 | 30.6 | 49.8 | 0 | 0 | - | - | 35.5 | 44.8 | 224 | 216 | 53.2 | 52.8 | 65.3 | 23.2 | 40 | 2.29 | 10 | 23.9 | 52.9 | 69.2 | 23.3 | 43.4 | 2.52 | 9.2 | 24.7 | 21.5 | 23.3 | 28.5 | 2.4 | 1.09 | 2.58 | 1.12 | 224 | 216 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:45:00 | 3981.06 | 97.78 | 787186.4 | 755473.5 | 41.78 | 432.372 | 4040.454 | 690.074 | 91 | 175 | 31.9 | 47.8 | 30.2 | 50.2 | 0 | 0 | - | - | 35.2 | 45.1 | 224 | 216 | 53.8 | 53.6 | 65.4 | 23.2 | 39.9 | 2.29 | 10 | 24 | 53.4 | 69.2 | 23.2 | 43.5 | 2.53 | 9.2 | 24.6 | 21.3 | 23.3 | 28.8 | 2.39 | 1.08 | 2.58 | 1.11 | 224 | 216 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:50:00 | 4034.52 | 97.78 | 787239.84 | 755473.5 | 42.47 | 387.642 | 4085.184 | 527.199 | 92 | 176 | 31.6 | 48.2 | 29.9 | 50.5 | 0 | 0 | - | - | 35 | 45.3 | 224 | 216 | 53.3 | 53.1 | 65.6 | 23.1 | 40.1 | 2.29 | 9.8 | 24.2 | 53.5 | 69.3 | 23.1 | 43.5 | 2.52 | 9.2 | 24.7 | 21.2 | 23.2 | 28.6 | 2.38 | 1.08 | 2.58 | 1.11 | 224 | 216 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 14:55:00 | 4074.26 | 97.78 | 787279.3 | 755473.5 | 43.16 | 342.914 | 4129.912 | 494.562 | 93 | 176 | 31.2 | 48.5 | 29.7 | 50.8 | 0 | 0 | - | - | 34.7 | 45.5 | 224 | 216 | 53.8 | 53.6 | 65.5 | 22.8 | 40 | 2.29 | 10 | 24.1 | 53.5 | 69.5 | 22.9 | 43.6 | 2.53 | 9.2 | 24.8 | 21.2 | 23.1 | 28.8 | 2.37 | 1.07 | 2.58 | 1.11 | 224 | 216 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:00:00 | 4086.7 | 98.26 | 787290.98 | 755473.98 | 43.83 | 305.642 | 4167.184 | 16.313 | 94 | 176 | 30.9 | 48.7 | 29.5 | 50.8 | 0 | 0 | - | - | 34.5 | 45.6 | 224 | 216 | 53.6 | 53.6 | 65.1 | 22.7 | 39.4 | 2.25 | 10.1 | 24.4 | 53.5 | 69.3 | 22.8 | 43.4 | 2.52 | 9.2 | 24.9 | 21 | 22.8 | 28.4 | 2.34 | 1.07 | 2.56 | 1.1 | 224 | 216 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:05:00 | 4086.86 | 99 | 787291.14 | 755474.72 | 44.49 | 298.188 | 4174.638 | -13.635 | 93 | 176 | 30.4 | 49.1 | 29.5 | 50.7 | 0 | 0 | - | - | 34.3 | 45.7 | 224 | 216 | 52 | 51.6 | 64 | 22.6 | 38.6 | 2.2 | 9.8 | 24 | 52 | 68.7 | 22.7 | 42.9 | 2.47 | 8.9 | 25 | 20.7 | 22.7 | 27.2 | 2.3 | 1.06 | 2.53 | 1.1 | 224 | 216 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:10:00 | 4086.86 | 100.08 | 787291.14 | 755475.82 | 45.17 | 305.643 | 4167.183 | -13.174 | 93 | 176 | 30.2 | 49.3 | 29.3 | 50.7 | 0 | 0 | - | - | 34.1 | 45.8 | 224 | 216 | 54.7 | 54.7 | 64.9 | 22.3 | 39.3 | 2.26 | 10.4 | 24 | 54.7 | 69.1 | 22.3 | 43.3 | 2.53 | 9.5 | 24.4 | 20.4 | 22.4 | 27.2 | 2.36 | 1.03 | 2.6 | 1.07 | 224 | 216 | 2740 | 2751
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:15:00 | 4086.86 | 101.26 | 787291.14 | 755476.98 | 45.97 | 342.914 | 4129.912 | -12.308 | 93 | 176 | 30 | 49.4 | 29.1 | 50.7 | 0 | 0 | - | - | 33.9 | 45.9 | 224 | 216 | 56.2 | 56.2 | 66.3 | 21.7 | 39.9 | 2.29 | 9.8 | 24.9 | 56 | 71.3 | 21.7 | 44.1 | 2.56 | 9.3 | 26 | 19.7 | 21.7 | 27 | 2.38 | 1.04 | 2.62 | 1.06 | 224 | 216 | 2844 | 2844
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:20:00 | 4086.86 | 102.3 | 787291.14 | 755478.08 | 46.78 | 342.914 | 4129.912 | -22.961 | 93 | 176 | 29.8 | 49.3 | 29 | 50.7 | 0 | 0 | - | - | 33.7 | 46 | 224 | 216 | 56.3 | 56.2 | 66.2 | 21.2 | 40.1 | 2.29 | 9.5 | 24.7 | 56.5 | 71.3 | 21.2 | 44 | 2.56 | 9.1 | 26 | 19.2 | 21.3 | 27.1 | 2.39 | 1.03 | 2.63 | 1.05 | 224 | 216 | 2832 | 2832
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:25:00 | 4086.92 | 103.4 | 787291.2 | 755479.18 | 47.6 | 342.914 | 4129.912 | -12.318 | 93 | 176 | 29.7 | 49.3 | 28.8 | 50.7 | 0 | 0 | - | - | 33.5 | 46.1 | 224 | 216 | 57.2 | 57.2 | 67 | 20.9 | 40.1 | 2.29 | 10 | 25.4 | 57.5 | 71.9 | 20.9 | 44.1 | 2.57 | 9.2 | 26.6 | 19.1 | 21.1 | 27.7 | 2.38 | 1.01 | 2.61 | 1.04 | 224 | 216 | 2832 | 2832
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:30:00 | 4086.94 | 104.56 | 787291.22 | 755480.3 | 48.41 | 342.914 | 4129.912 | -12.834 | 93 | 176 | 29.5 | 49.2 | 28.6 | 50.6 | 0 | 0 | - | - | 33.4 | 46.2 | 224 | 216 | 57.2 | 57.2 | 67 | 20.7 | 40 | 2.3 | 9.8 | 25.3 | 56.9 | 71.7 | 20.7 | 44 | 2.57 | 9.1 | 26.3 | 18.8 | 20.8 | 27.9 | 2.42 | 1.01 | 2.62 | 1.03 | 224 | 216 | 2844 | 2844
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:35:00 | 4086.98 | 105.64 | 787291.26 | 755481.38 | 49.24 | 342.914 | 4129.912 | -12.24 | 93 | 176 | 29.4 | 49.2 | 28.4 | 50.6 | 0 | 0 | - | - | 33.2 | 46.2 | 224 | 216 | 58.9 | 58.7 | 68.6 | 20.5 | 41.4 | 2.38 | 9.8 | 25.6 | 58.9 | 72.9 | 20.6 | 44.7 | 2.61 | 9.3 | 26.9 | 18.6 | 20.7 | 30.2 | 2.48 | 1 | 2.67 | 1.02 | 224 | 216 | 2953 | 2910
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:40:00 | 4086.98 | 106.66 | 787291.26 | 755482.42 | 50.11 | 313.098 | 4159.728 | -13.247 | 93 | 176 | 29.2 | 49.1 | 28.3 | 50.5 | 0 | 0 | - | - | 33.1 | 46.3 | 224 | 216 | 59.9 | 59.8 | 69.1 | 20.2 | 41.4 | 2.38 | 9.6 | 26.1 | 59.9 | 73.8 | 20.2 | 45 | 2.62 | 9.3 | 27.6 | 18.2 | 20.2 | 30.1 | 2.49 | 1 | 2.67 | 1.01 | 224 | 216 | 2974 | 3000
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:45:00 | 4086.98 | 107.52 | 787291.26 | 755483.26 | 51 | 313.098 | 4159.728 | -11.315 | 93 | 176 | 29.1 | 49 | 28.1 | 50.4 | 0 | 0 | - | - | 33.1 | 46.2 | 224 | 216 | 58.9 | 58.8 | 68.4 | 19.8 | 40.9 | 2.35 | 9.3 | 26 | 58.5 | 73.7 | 19.9 | 44.6 | 2.6 | 9.1 | 27.9 | 17.9 | 19.9 | 29.4 | 2.47 | 0.99 | 2.67 | 1 | 224 | 216 | 2985 | 3000
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:50:00 | 4086.98 | 108.62 | 787291.26 | 755484.36 | 51.88 | 313.098 | 4159.728 | -13.318 | 93 | 176 | 28.9 | 48.9 | 27.9 | 50.3 | 0 | 0 | - | - | 33 | 46.2 | 224 | 216 | 59.9 | 59.9 | 69 | 19.6 | 41.3 | 2.37 | 9.5 | 26.3 | 60 | 73.8 | 19.7 | 44.9 | 2.61 | 9.1 | 27.8 | 17.7 | 19.7 | 30.5 | 2.45 | 0.98 | 2.66 | 1 | 224 | 216 | 2971 | 2995
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 15:55:00 | 4086.98 | 109.76 | 787291.26 | 755485.5 | 52.76 | 342.914 | 4129.912 | -13.725 | 93 | 176 | 28.8 | 48.8 | 27.8 | 50.2 | 0 | 0 | - | - | 32.9 | 46.2 | 224 | 216 | 59.9 | 59.9 | 69 | 19.3 | 41.1 | 2.36 | 9.6 | 26.3 | 60 | 73.9 | 19.4 | 44.9 | 2.61 | 9.2 | 27.9 | 17.4 | 19.4 | 30.4 | 2.45 | 0.98 | 2.66 | 0.99 | 224 | 216 | 3000 | 3000
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:00:00 | 4086.98 | 110.78 | 787291.26 | 755486.5 | 53.25 | 342.914 | 4129.912 | -13.833 | 93 | 176 | 28.7 | 48.9 | 27.6 | 50.4 | 0 | 0 | - | - | 32.9 | 46.1 | 0 | 0 | 0 | 0 | 54.4 | 23 | 31.1 | 1.62 | 3.8 | 26.6 | 0 | 59.3 | 23 | 34.1 | 1.78 | 3.9 | 29 | 21 | 21 | 29.7 | 1.6 | 1.38 | 1.71 | 1.38 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:05:00 | 4086.98 | 111.88 | 787291.26 | 755487.62 | 53.46 | 313.098 | 4159.728 | -11.871 | 93 | 176 | 28.4 | 49.5 | 27.5 | 50.9 | 0 | 0 | - | - | 32.8 | 46.1 | 0 | 0 | 0 | 0 | 30.8 | 37.7 | 29.4 | 1.42 | 14.8 | 7.9 | 0 | 30.9 | 41.2 | 30.9 | 1.47 | 18.1 | 7.3 | 23 | 22.9 | 29.1 | 1.46 | 1.46 | 1.47 | 1.47 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:10:00 | 4086.98 | 113 | 787291.26 | 755488.74 | 53.67 | 313.098 | 4159.728 | -11.903 | 93 | 176 | 28.1 | 50.2 | 27.4 | 51.3 | 0 | 0 | - | - | 32.7 | 46.2 | 0 | 0 | 0 | 0 | 29.9 | 36.7 | 29.4 | 1.44 | 13.1 | 6.5 | 0 | 29.8 | 40.9 | 30.2 | 1.46 | 17.2 | 6.5 | 23.5 | 23.5 | 28.9 | 1.48 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:15:00 | 4086.98 | 114.02 | 787291.26 | 755489.8 | 53.86 | 313.098 | 4159.728 | -14.39 | 93 | 176 | 27.9 | 50.8 | 27.4 | 51.5 | 0 | 0 | - | - | 32.7 | 46.2 | 0 | 0 | 0 | 0 | 29.7 | 35.8 | 29.4 | 1.46 | 11.9 | 5.9 | 0 | 30.1 | 38.7 | 29.7 | 1.47 | 14.7 | 6.4 | 23.8 | 23.7 | 28.7 | 1.49 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:20:00 | 4086.98 | 115.12 | 787291.26 | 755490.88 | 54.05 | 313.098 | 4159.728 | -15.163 | 93 | 176 | 27.7 | 51.1 | 27.3 | 51.7 | 0 | 0 | - | - | 32.6 | 46.2 | 0 | 0 | 0 | 0 | 29.4 | 35.6 | 29.3 | 1.47 | 11.5 | 5.4 | 0 | 30.2 | 37.3 | 29.3 | 1.48 | 13 | 6.3 | 23.9 | 23.9 | 28.6 | 1.5 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:25:00 | 4087.06 | 116.36 | 787291.34 | 755492.08 | 54.22 | 342.914 | 4129.912 | -8.283 | 93 | 176 | 27.6 | 51.3 | 27.3 | 51.8 | 0 | 0 | - | - | 32.5 | 46.2 | 0 | 0 | 0 | 0 | 29.3 | 35.4 | 29.3 | 1.47 | 11.2 | 5.2 | 0 | 30.1 | 36.6 | 29.1 | 1.48 | 12.3 | 6.1 | 24.1 | 24 | 28.8 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:30:00 | 4087.06 | 117.38 | 787291.34 | 755493.12 | 54.39 | 313.098 | 4159.728 | -12.601 | 93 | 176 | 27.6 | 51.4 | 27.3 | 52 | 0 | 0 | - | - | 32.4 | 46.2 | 0 | 0 | 0 | 0 | 29.4 | 35.1 | 29.3 | 1.47 | 10.8 | 5.3 | 0 | 29.9 | 36.5 | 28.8 | 1.49 | 12.1 | 5.9 | 24.1 | 24.1 | 28.8 | 1.5 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:35:00 | 4087.08 | 118.48 | 787291.36 | 755494.2 | 54.55 | 342.914 | 4129.912 | -11.614 | 93 | 176 | 27.6 | 51.4 | 27.2 | 52 | 0 | 0 | - | - | 32.3 | 46.3 | 0 | 0 | 0 | 0 | 29.3 | 34.7 | 29.2 | 1.47 | 10.4 | 5.2 | 0 | 29.7 | 36.1 | 28.7 | 1.49 | 11.7 | 5.6 | 24.2 | 24.1 | 28.6 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:40:00 | 4087.08 | 119.54 | 787291.36 | 755495.28 | 54.71 | 313.098 | 4159.728 | -13.916 | 93 | 176 | 27.5 | 51.5 | 27.2 | 52.1 | 0 | 0 | - | - | 32.3 | 46.3 | 0 | 0 | 0 | 0 | 29.2 | 34.4 | 29.1 | 1.47 | 10 | 5 | 0 | 29.4 | 35.4 | 28.6 | 1.49 | 10.9 | 5.4 | 24.2 | 24.2 | 28.3 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:45:00 | 4087.08 | 120.64 | 787291.36 | 755496.4 | 54.86 | 313.098 | 4159.728 | -13.947 | 93 | 176 | 27.4 | 51.7 | 27.1 | 52.2 | 0 | 0 | - | - | 32.2 | 46.4 | 0 | 0 | 0 | 0 | 29.1 | 34.3 | 28.9 | 1.48 | 9.8 | 4.7 | 0 | 29.3 | 34.9 | 28.4 | 1.49 | 10.3 | 5.1 | 24.2 | 24.2 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:50:00 | 4087.08 | 123.24 | 787291.36 | 755499.4 | 55 | 342.914 | 4129.912 | -218.477 | 93 | 176 | 27.3 | 51.8 | 27.1 | 52.2 | 0 | 0 | - | - | 32.1 | 46.4 | 0 | 0 | 0 | 0 | 28.9 | 34.1 | 28.8 | 1.48 | 9.7 | 4.6 | 0 | 29.2 | 34.2 | 28.4 | 1.49 | 9.6 | 5.1 | 24.2 | 24.2 | 27.9 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 16:55:00 | 4087.08 | 146.4 | 787291.36 | 755523.08 | 55.14 | 387.642 | 4085.184 | -625.958 | 92 | 176 | 27.3 | 51.9 | 27.1 | 52.2 | 0 | 0 | - | - | 32 | 46.5 | 0 | 0 | 0 | 0 | 28.7 | 34.1 | 28.7 | 1.48 | 9.6 | 4.4 | 0 | 29.1 | 33.6 | 28.3 | 1.49 | 9.1 | 5 | 24.3 | 24.2 | 28 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:00:00 | 4087.08 | 207.62 | 787291.36 | 755585.92 | 55.29 | 462.188 | 4010.638 | -826.779 | 91 | 176 | 27.2 | 52 | 27 | 52.2 | 0 | 0 | - | - | 32 | 46.5 | 0 | 0 | 0 | 0 | 28.7 | 33.9 | 28.7 | 1.48 | 9.4 | 4.3 | 0 | 29 | 33.1 | 28.3 | 1.49 | 8.6 | 4.8 | 24.3 | 24.2 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:05:00 | 4087.08 | 278.44 | 787291.36 | 755654.98 | 55.45 | 529.281 | 3943.546 | -842.508 | 89 | 176 | 27.2 | 52.1 | 27.1 | 52.2 | 0 | 0 | - | - | 32 | 46.5 | 0 | 0 | 0 | 0 | 28.7 | 33.6 | 28.8 | 1.48 | 9.1 | 4.4 | 0 | 29 | 32.9 | 28.3 | 1.49 | 8.2 | 4.8 | 24.3 | 24.3 | 28.4 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:10:00 | 4087.08 | 347.16 | 787291.36 | 755725.36 | 55.6 | 618.741 | 3854.085 | -832.822 | 88 | 176 | 27.1 | 52.1 | 27.1 | 52.2 | 0 | 0 | - | - | 31.9 | 46.5 | 0 | 0 | 0 | 0 | 29 | 33.2 | 28.9 | 1.48 | 8.5 | 4.5 | 0 | 29.1 | 32.4 | 28.3 | 1.5 | 7.7 | 4.8 | 24.4 | 24.4 | 28.7 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:15:00 | 4087.08 | 415.96 | 787291.36 | 755793.76 | 55.76 | 670.921 | 3801.905 | -821.127 | 86 | 176 | 27.1 | 52.2 | 27.2 | 52.2 | 0 | 0 | - | - | 31.9 | 46.5 | 0 | 0 | 0 | 0 | 29.2 | 32.8 | 29.1 | 1.48 | 8.1 | 4.7 | 0 | 29.1 | 32.1 | 28.2 | 1.5 | 7.2 | 4.8 | 24.5 | 24.5 | 28.3 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:20:00 | 4087.08 | 485.72 | 787291.36 | 755862.72 | 55.91 | 760.379 | 3712.447 | -830.601 | 85 | 176 | 27.2 | 52.2 | 27.2 | 52.1 | 0 | 0 | - | - | 31.8 | 46.5 | 0 | 0 | 0 | 0 | 29.2 | 32.4 | 28.9 | 1.49 | 7.5 | 4.6 | 0 | 29.1 | 31.7 | 28.3 | 1.5 | 6.7 | 4.7 | 24.6 | 24.6 | 28.2 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:25:00 | 4087.08 | 555.08 | 787291.36 | 755932.52 | 56.06 | 805.105 | 3667.721 | -832.076 | 83 | 176 | 27.2 | 52.3 | 27.3 | 52.1 | 0 | 0 | - | - | 31.8 | 46.6 | 0 | 0 | 0 | 0 | 29.4 | 31.9 | 29 | 1.49 | 7 | 4.7 | 0 | 29.2 | 31.2 | 28.3 | 1.51 | 6.2 | 4.7 | 24.7 | 24.7 | 28.1 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:30:00 | 4087.08 | 625.02 | 787291.36 | 756001.62 | 56.22 | 894.564 | 3578.262 | -833.117 | 82 | 176 | 27.2 | 52.3 | 27.4 | 52 | 0 | 0 | - | - | 31.8 | 46.6 | 0 | 0 | 0 | 0 | 29.6 | 31.4 | 29.1 | 1.5 | 6.4 | 4.8 | 0 | 29.2 | 30.8 | 28.3 | 1.51 | 5.7 | 4.6 | 24.8 | 24.8 | 27.8 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:35:00 | 4087.08 | 694.38 | 787291.36 | 756071.82 | 56.37 | 961.655 | 3511.171 | -829.553 | 80 | 176 | 27.2 | 52.3 | 27.4 | 52 | 0 | 0 | - | - | 31.8 | 46.5 | 0 | 0 | 0 | 0 | 29.7 | 31.2 | 29.1 | 1.5 | 6.1 | 4.7 | 0 | 29.3 | 30.6 | 28.3 | 1.52 | 5.3 | 4.5 | 24.9 | 24.9 | 27.7 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:40:00 | 4087.08 | 763.3 | 787291.36 | 756139.88 | 56.52 | 1036.203 | 3436.623 | -832.755 | 78 | 176 | 27.3 | 52.3 | 27.4 | 52 | 0 | 0 | - | - | 31.8 | 46.5 | 0 | 0 | 0 | 0 | 29.7 | 31.1 | 29.1 | 1.51 | 5.8 | 4.6 | 0 | 29.3 | 30.3 | 28.3 | 1.52 | 5.1 | 4.5 | 25 | 25 | 27.7 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:45:00 | 4087.08 | 832.06 | 787291.36 | 756209.94 | 56.67 | 1125.66 | 3347.167 | -835.827 | 77 | 176 | 27.3 | 52.4 | 27.3 | 52.3 | 0 | 0 | - | - | 31.8 | 46.5 | 0 | 0 | 0 | 0 | 29.8 | 30.8 | 29.1 | 1.51 | 5.6 | 4.7 | 0 | 29.3 | 30.2 | 28.3 | 1.52 | 4.9 | 4.4 | 25.1 | 25.1 | 27.9 | 1.54 | 1.55 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:50:00 | 4087.08 | 902.74 | 787291.36 | 756278.88 | 56.82 | 1192.752 | 3280.074 | -848.239 | 75 | 176 | 27.3 | 52.4 | 27.4 | 52.3 | 0 | 0 | - | - | 31.8 | 46.6 | 0 | 0 | 0 | 0 | 29.9 | 30.7 | 29.2 | 1.51 | 5.3 | 4.7 | 0 | 29.4 | 30.2 | 28.3 | 1.52 | 4.7 | 4.4 | 25.2 | 25.3 | 27.8 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 17:55:00 | 4087.08 | 972 | 787291.36 | 756349.4 | 56.97 | 1252.39 | 3220.436 | -849.518 | 74 | 176 | 27.3 | 52.4 | 27.6 | 52 | 0 | 0 | - | - | 31.8 | 46.6 | 0 | 0 | 0 | 0 | 29.9 | 30.6 | 29.2 | 1.51 | 5.2 | 4.8 | 0 | 29.4 | 30.1 | 28.4 | 1.52 | 4.6 | 4.4 | 25.4 | 25.4 | 27.8 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:00:00 | 4087.08 | 1041.24 | 787291.36 | 756418.72 | 57.13 | 1334.391 | 3138.435 | -870.602 | 72 | 176 | 27.4 | 52.4 | 27.7 | 51.9 | 0 | 0 | - | - | 31.7 | 46.6 | 0 | 0 | 0 | 0 | 30 | 30.4 | 29.2 | 1.51 | 5 | 4.7 | 0 | 29.4 | 30 | 28.5 | 1.53 | 4.5 | 4.4 | 25.5 | 25.5 | 27.7 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:05:00 | 4087.08 | 1114.7 | 787291.36 | 756491.3 | 57.28 | 1416.395 | 3056.431 | -866.752 | 70 | 176 | 27.4 | 52.5 | 27.8 | 51.9 | 0 | 0 | - | - | 31.7 | 46.6 | 0 | 0 | 0 | 0 | 30 | 30.2 | 29.2 | 1.51 | 4.9 | 4.9 | 0 | 29.4 | 29.8 | 28.6 | 1.53 | 4.2 | 4.3 | 25.6 | 25.6 | 27.2 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:10:00 | 4087.08 | 1185.82 | 787291.36 | 756562.82 | 57.44 | 1483.487 | 2989.339 | -830.619 | 69 | 176 | 27.4 | 52.5 | 27.7 | 52.1 | 0 | 0 | - | - | 31.7 | 46.5 | 0 | 0 | 0 | 0 | 29.9 | 30.1 | 29.1 | 1.51 | 4.6 | 4.7 | 0 | 29.3 | 29.7 | 28.4 | 1.53 | 4 | 4.2 | 25.7 | 25.7 | 27.4 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:15:00 | 4087.08 | 1255.02 | 787291.36 | 756631.2 | 57.59 | 1558.034 | 2914.792 | -814.45 | 67 | 176 | 27.4 | 52.6 | 27.7 | 52.2 | 0 | 0 | - | - | 31.7 | 46.6 | 0 | 0 | 0 | 0 | 29.9 | 29.9 | 29.1 | 1.52 | 4.4 | 4.6 | 0 | 29.3 | 29.6 | 28.3 | 1.54 | 3.8 | 4.1 | 25.7 | 25.8 | 27.4 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:20:00 | 4087.08 | 1325.54 | 787291.36 | 756701.74 | 57.75 | 1640.035 | 2832.791 | -840.634 | 66 | 176 | 27.4 | 52.6 | 27.9 | 52 | 0 | 0 | - | - | 31.6 | 46.6 | 0 | 0 | 0 | 0 | 29.9 | 29.8 | 28.9 | 1.52 | 4.3 | 4.5 | 0 | 29.3 | 29.4 | 28.3 | 1.54 | 3.6 | 4 | 25.8 | 25.8 | 27.3 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:25:00 | 4087.08 | 1394.56 | 787291.36 | 756771.6 | 57.91 | 1692.219 | 2780.607 | -836.124 | 64 | 176 | 27.4 | 52.7 | 28 | 51.9 | 0 | 0 | - | - | 31.6 | 46.7 | 0 | 0 | 0 | 0 | 29.8 | 29.8 | 28.8 | 1.52 | 4.2 | 4.3 | 0 | 29.2 | 29.3 | 28.3 | 1.54 | 3.5 | 3.8 | 25.8 | 25.8 | 27.2 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:30:00 | 4087.08 | 1463.66 | 787291.36 | 756840.24 | 58.06 | 1774.22 | 2698.606 | -837.8 | 63 | 176 | 27.4 | 52.7 | 28.1 | 51.9 | 0 | 0 | - | - | 31.5 | 46.7 | 0 | 0 | 0 | 0 | 29.8 | 29.8 | 28.9 | 1.53 | 4.2 | 4.3 | 0 | 29.2 | 29.3 | 28.3 | 1.54 | 3.4 | 3.8 | 25.9 | 25.8 | 27.3 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:35:00 | 4087.08 | 1536.66 | 787291.36 | 756914.06 | 58.22 | 1863.677 | 2609.149 | -1087.804 | 61 | 176 | 27.4 | 52.8 | 28.1 | 51.8 | 0 | 0 | - | - | 31.4 | 46.8 | 0 | 0 | 0 | 0 | 29.7 | 29.7 | 28.7 | 1.52 | 4.1 | 4.2 | 0 | 29.2 | 29.2 | 28.2 | 1.55 | 3.3 | 3.7 | 25.9 | 25.8 | 26.8 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:40:00 | 4087.08 | 1626.24 | 787291.36 | 757004.66 | 58.39 | 1953.133 | 2519.693 | -1063.28 | 59 | 176 | 27.4 | 52.8 | 28.2 | 51.8 | 0 | 0 | - | - | 31.4 | 46.8 | 0 | 0 | 0 | 0 | 29.6 | 29.6 | 28.6 | 1.53 | 3.9 | 4 | 0 | 29 | 29.2 | 28.1 | 1.55 | 3.2 | 3.5 | 25.9 | 25.9 | 27 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:45:00 | 4087.08 | 1714.24 | 787291.36 | 757091.06 | 58.55 | 2042.591 | 2430.235 | -1071.357 | 57 | 176 | 27.4 | 52.8 | 28.3 | 51.7 | 0 | 0 | - | - | 31.4 | 46.9 | 0 | 0 | 0 | 0 | 29.5 | 29.6 | 28.6 | 1.53 | 3.8 | 3.9 | 0 | 28.9 | 29.2 | 28.1 | 1.55 | 3.2 | 3.5 | 25.9 | 25.8 | 27.1 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:50:00 | 4087.08 | 1808.24 | 787291.36 | 757185.26 | 58.72 | 2161.866 | 2310.961 | -1298.483 | 55 | 176 | 27.5 | 52.9 | 28.3 | 51.7 | 0 | 0 | - | - | 31.3 | 46.9 | 0 | 0 | 0 | 0 | 29.4 | 29.6 | 28.7 | 1.53 | 3.8 | 3.8 | 0 | 28.9 | 29.2 | 28.1 | 1.55 | 3.2 | 3.4 | 25.9 | 25.8 | 27.1 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 18:55:00 | 4087.08 | 1911.88 | 787291.36 | 757290.2 | 58.9 | 2273.687 | 2199.14 | -1278.626 | 52 | 176 | 27.5 | 52.9 | 28.4 | 51.6 | 0 | 0 | - | - | 31.3 | 46.9 | 0 | 0 | 0 | 0 | 29.4 | 29.6 | 28.8 | 1.53 | 3.8 | 3.7 | 0 | 28.9 | 29.3 | 28.1 | 1.55 | 3.3 | 3.3 | 25.9 | 25.9 | 27.2 | 1.57 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:00:00 | 4087.08 | 2032.9 | 787291.36 | 757412.54 | 59.09 | 2415.325 | 2057.501 | -1545.628 | 49 | 176 | 27.5 | 52.9 | 28.5 | 51.6 | 0 | 0 | - | - | 31.3 | 46.9 | 0 | 0 | 0 | 0 | 29.4 | 29.6 | 28.9 | 1.53 | 3.7 | 3.7 | 0 | 28.8 | 29.3 | 28.1 | 1.55 | 3.3 | 3.3 | 25.9 | 25.9 | 27.2 | 1.57 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:05:00 | 4087.08 | 2162.48 | 787291.36 | 757540.54 | 59.3 | 2549.513 | 1923.313 | -1483.427 | 46 | 176 | 27.6 | 52.9 | 28.7 | 51.4 | 0 | 0 | - | - | 31.2 | 47 | 0 | 0 | 0 | 0 | 29.4 | 29.5 | 28.8 | 1.54 | 3.6 | 3.6 | 0 | 28.8 | 29.3 | 28.2 | 1.55 | 3.2 | 3.3 | 26 | 26 | 27.2 | 1.57 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:10:00 | 4087.08 | 2287.22 | 787291.36 | 757663.72 | 59.52 | 2676.242 | 1796.584 | -1489.538 | 44 | 176 | 27.7 | 52.8 | 28.9 | 51.2 | 0 | 0 | - | - | 31.3 | 47 | 0 | 0 | 0 | 0 | 29.4 | 29.4 | 28.8 | 1.54 | 3.5 | 3.6 | 0 | 28.8 | 29.2 | 28.2 | 1.55 | 3.1 | 3.2 | 26.2 | 26.1 | 27.2 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:15:00 | 4087.08 | 2409.7 | 787291.36 | 757787.72 | 59.73 | 2795.517 | 1677.309 | -1493.031 | 41 | 176 | 27.7 | 52.8 | 29.1 | 51 | 0 | 0 | - | - | 31.3 | 46.9 | 0 | 0 | 0 | 0 | 29.2 | 29.4 | 28.7 | 1.54 | 3.4 | 3.4 | 0 | 28.8 | 29.2 | 28.2 | 1.56 | 2.9 | 3.1 | 26.3 | 26.2 | 27.4 | 1.58 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:20:00 | 4087.08 | 2543.86 | 787291.36 | 757922.26 | 59.96 | 2944.611 | 1528.215 | -1704.557 | 37 | 176 | 27.8 | 52.8 | 29.3 | 50.8 | 0 | 0 | - | - | 31.3 | 46.9 | 0 | 0 | 0 | 0 | 29.2 | 29.4 | 28.7 | 1.54 | 3.3 | 3.3 | 0 | 28.8 | 29.2 | 28.3 | 1.56 | 2.8 | 3 | 26.5 | 26.5 | 27.5 | 1.58 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:25:00 | 4087.08 | 2688.22 | 787291.36 | 758066.74 | 60.21 | 3078.795 | 1394.031 | -1778.217 | 34 | 176 | 28 | 52.8 | 29.5 | 50.6 | 0 | 0 | - | - | 31.4 | 46.9 | 0 | 0 | 0 | 0 | 29.3 | 29.4 | 28.7 | 1.55 | 3.1 | 3.3 | 0 | 28.8 | 29.1 | 28.4 | 1.57 | 2.6 | 2.9 | 26.8 | 26.7 | 27.6 | 1.59 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:30:00 | 4087.08 | 2835.34 | 787291.36 | 758211.92 | 60.71 | 3212.981 | 1259.845 | -1712.604 | 31 | 176 | 28 | 52.8 | 29.7 | 50.4 | 0 | 0 | - | - | 31.5 | 46.9 | 219 | 206 | 54.6 | 54.5 | 63.5 | 25.9 | 42.2 | 2.39 | 11.9 | 20.5 | 53.6 | 65.1 | 25.9 | 44.4 | 2.57 | 11.6 | 19.9 | 23.2 | 25.4 | 28.7 | 2.41 | 1.11 | 2.58 | 1.13 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:35:00 | 4087.08 | 2975.4 | 787291.36 | 758352.86 | 61.4 | 3362.076 | 1110.751 | -1703.243 | 27 | 176 | 28.1 | 52.7 | 29.9 | 50.1 | 0 | 0 | - | - | 31.6 | 46.8 | 220 | 206 | 53.7 | 53.4 | 66.3 | 23.9 | 40.5 | 2.31 | 10.7 | 24.5 | 53.5 | 70.1 | 24 | 43.6 | 2.53 | 10.3 | 25.5 | 22.1 | 23.9 | 28.8 | 2.41 | 1.08 | 2.58 | 1.1 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:40:00 | 4087.08 | 3118.06 | 787291.36 | 758497.32 | 62.09 | 3518.624 | 954.202 | -1711.985 | 24 | 176 | 28.2 | 52.5 | 30.1 | 49.9 | 0 | 0 | - | - | 31.7 | 46.7 | 220 | 206 | 54.1 | 54 | 66.6 | 23.6 | 40.4 | 2.31 | 10.4 | 24.7 | 54 | 70.7 | 23.6 | 43.6 | 2.53 | 10 | 26 | 21.8 | 23.7 | 28.9 | 2.41 | 1.08 | 2.59 | 1.1 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:45:00 | 4087.08 | 3261.5 | 787291.36 | 758641.7 | 62.79 | 3652.812 | 820.014 | -1748.959 | 21 | 176 | 28.4 | 52.4 | 30.2 | 49.7 | 0 | 0 | - | - | 31.7 | 46.7 | 220 | 206 | 53.6 | 53.5 | 66.4 | 23.6 | 40.1 | 2.31 | 10.3 | 24.6 | 53.5 | 70.7 | 23.6 | 43.6 | 2.53 | 9.9 | 26 | 21.8 | 23.7 | 28.4 | 2.41 | 1.08 | 2.59 | 1.1 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:50:00 | 4087.08 | 3398.68 | 787291.36 | 758778.56 | 63.48 | 3831.722 | 641.104 | -1604.149 | 16 | 176 | 28.5 | 52.3 | 30.4 | 49.5 | 0 | 0 | - | - | 31.8 | 46.6 | 220 | 206 | 53.1 | 53 | 65.9 | 23.7 | 39.9 | 2.28 | 10.3 | 24.6 | 53 | 70.4 | 23.8 | 43.4 | 2.52 | 10 | 25.9 | 21.9 | 23.9 | 27.9 | 2.38 | 1.09 | 2.58 | 1.11 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 19:55:00 | 4087.08 | 3517.82 | 787291.36 | 758895.58 | 64.18 | 3973.365 | 499.461 | -1138.136 | 12 | 176 | 28.6 | 52.1 | 30.5 | 49.4 | 0 | 0 | - | - | 32 | 46.6 | 220 | 206 | 54.3 | 54.5 | 66.8 | 23.9 | 40.4 | 2.32 | 10.5 | 24.7 | 54.5 | 71 | 24 | 43.9 | 2.56 | 10 | 25.8 | 22.3 | 24.2 | 29.5 | 2.42 | 1.09 | 2.61 | 1.11 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:00:00 | 4087.08 | 3610.82 | 787291.36 | 758988.8 | 64.88 | 4070.274 | 402.552 | -1081.955 | 10 | 176 | 28.8 | 52 | 30.6 | 49.3 | 0 | 0 | - | - | 32 | 46.5 | 220 | 206 | 54.6 | 54.5 | 67 | 24.2 | 40.6 | 2.32 | 10.6 | 25 | 54.5 | 71.2 | 24.2 | 44.1 | 2.56 | 10.1 | 26 | 22.5 | 24.4 | 29.4 | 2.41 | 1.1 | 2.61 | 1.12 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:05:00 | 4087.08 | 3700.56 | 787291.36 | 759077.98 | 65.58 | 4159.728 | 313.098 | -1113.39 | 8 | 176 | 28.9 | 51.9 | 30.6 | 49.3 | 0 | 0 | - | - | 32.1 | 46.5 | 220 | 206 | 54.5 | 54.5 | 66.7 | 24.3 | 40.6 | 2.33 | 10.7 | 24.6 | 54.8 | 71.1 | 24.3 | 44 | 2.57 | 10.1 | 25.8 | 22.6 | 24.5 | 29.6 | 2.42 | 1.1 | 2.62 | 1.12 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:10:00 | 4087.08 | 3757.84 | 787291.36 | 759134.4 | 66.28 | 4189.548 | 283.278 | -419.666 | 7 | 176 | 28.9 | 51.8 | 30.7 | 49.3 | 0 | 0 | - | - | 32.2 | 46.4 | 220 | 206 | 54.5 | 54.4 | 66.5 | 24.4 | 40.4 | 2.32 | 10.6 | 24.5 | 54.3 | 71.2 | 24.5 | 44.1 | 2.56 | 10.2 | 26 | 22.7 | 24.6 | 29.2 | 2.41 | 1.11 | 2.62 | 1.13 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:15:00 | 4087.08 | 3790.18 | 787291.36 | 759166.16 | 66.97 | 4204.458 | 268.368 | -220.307 | 7 | 176 | 29 | 51.7 | 30.6 | 49.4 | 0 | 0 | - | - | 32.2 | 46.5 | 220 | 206 | 53 | 52.9 | 65.7 | 24.3 | 40 | 2.29 | 10.4 | 24.2 | 53.2 | 70.5 | 24.4 | 43.6 | 2.53 | 10 | 25.7 | 22.6 | 24.6 | 27.7 | 2.38 | 1.11 | 2.59 | 1.13 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:20:00 | 4087.08 | 3809.72 | 787291.36 | 759185.84 | 67.65 | 4204.458 | 268.368 | -254.244 | 7 | 176 | 29 | 51.7 | 30.4 | 49.7 | 0 | 0 | - | - | 32.3 | 46.5 | 220 | 206 | 53.3 | 53.4 | 65.7 | 24.2 | 40.1 | 2.3 | 10.5 | 24 | 53.2 | 70.5 | 24.3 | 43.7 | 2.55 | 10 | 25.5 | 22.4 | 24.4 | 28.2 | 2.39 | 1.1 | 2.6 | 1.12 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:25:00 | 4087.08 | 3828.28 | 787291.36 | 759204.6 | 68.34 | 4226.823 | 246.003 | -231.243 | 6 | 176 | 28.9 | 51.7 | 30.2 | 49.9 | 0 | 0 | - | - | 32.2 | 46.5 | 220 | 206 | 53.8 | 53.9 | 66.2 | 24.2 | 40.4 | 2.3 | 10.4 | 24.6 | 54 | 70.7 | 24.2 | 43.8 | 2.54 | 10.1 | 25.9 | 22.3 | 24.2 | 28.6 | 2.4 | 1.1 | 2.59 | 1.12 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:30:00 | 4087.08 | 3847.14 | 787291.36 | 759223.32 | 69.02 | 4249.188 | 223.638 | -231.06 | 6 | 176 | 28.9 | 51.7 | 30.1 | 50.1 | 0 | 0 | - | - | 32.2 | 46.6 | 220 | 206 | 52.7 | 52.9 | 65.6 | 23.9 | 39.7 | 2.27 | 10.4 | 24.5 | 53 | 70.5 | 24.1 | 43.6 | 2.52 | 10 | 25.8 | 22.2 | 24.1 | 27.7 | 2.35 | 1.1 | 2.57 | 1.12 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:35:00 | 4087.08 | 3866.64 | 787291.36 | 759242.6 | 69.69 | 4249.188 | 223.638 | -237.611 | 6 | 176 | 28.9 | 51.7 | 29.9 | 50.2 | 0 | 0 | - | - | 32.2 | 46.6 | 220 | 206 | 52.1 | 51.9 | 64.6 | 23.7 | 39.1 | 2.24 | 10.3 | 24.1 | 52 | 69.8 | 23.8 | 43.1 | 2.5 | 9.9 | 25.5 | 21.9 | 23.9 | 26.7 | 2.32 | 1.09 | 2.55 | 1.11 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:40:00 | 4087.08 | 3883.9 | 787291.36 | 759259.62 | 70.35 | 4249.188 | 223.638 | -10.522 | 5 | 176 | 28.9 | 51.7 | 29.7 | 50.3 | 0 | 0 | - | - | 32.2 | 46.7 | 220 | 206 | 52 | 51.9 | 64.3 | 23.6 | 39 | 2.23 | 10.3 | 23.9 | 52 | 69.3 | 23.7 | 42.9 | 2.5 | 9.9 | 25.2 | 21.7 | 23.7 | 26.6 | 2.32 | 1.08 | 2.54 | 1.1 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:45:00 | 4087.08 | 3884.5 | 787291.36 | 759260.24 | 71.01 | 4241.733 | 231.093 | -8.983 | 5 | 176 | 28.9 | 51.7 | 29.4 | 50.7 | 0 | 0 | - | - | 32.1 | 46.8 | 220 | 206 | 52 | 51.9 | 64.4 | 23.3 | 38.9 | 2.23 | 10.3 | 24.1 | 52 | 69.5 | 23.4 | 42.9 | 2.49 | 9.9 | 25.6 | 21.6 | 23.5 | 26.7 | 2.31 | 1.07 | 2.54 | 1.09 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:50:00 | 4087.08 | 3885.38 | 787291.36 | 759261.1 | 71.67 | 4249.188 | 223.638 | 9.081 | 5 | 176 | 28.8 | 51.6 | 29.2 | 50.9 | 0 | 0 | - | - | 32 | 46.9 | 220 | 206 | 52.1 | 51.9 | 64.3 | 23.2 | 38.8 | 2.22 | 10.3 | 24.1 | 52 | 69.4 | 23.2 | 42.7 | 2.48 | 9.8 | 25.4 | 21.3 | 23.2 | 26.6 | 2.31 | 1.07 | 2.53 | 1.09 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 20:55:00 | 4087.14 | 3885.92 | 787291.42 | 759261.64 | 72.32 | 4241.733 | 231.093 | -9.3 | 5 | 176 | 28.7 | 51.6 | 29.1 | 50.9 | 0 | 0 | - | - | 32 | 46.9 | 220 | 206 | 51.6 | 51.9 | 64.3 | 22.8 | 38.7 | 2.21 | 10.2 | 24.2 | 52 | 69.2 | 23.1 | 42.6 | 2.47 | 9.8 | 25.5 | 21.2 | 23.1 | 26.4 | 2.3 | 1.07 | 2.52 | 1.09 | 220 | 206 | 2400 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:00:00 | 4087.14 | 3886.34 | 787291.42 | 759262.1 | 72.98 | 4241.733 | 231.093 | -8.203 | 5 | 176 | 28.6 | 51.6 | 28.9 | 51 | 0 | 0 | - | - | 31.9 | 47 | 220 | 206 | 51.6 | 51.9 | 64.2 | 22.7 | 38.6 | 2.22 | 10.2 | 24 | 52 | 69.3 | 22.8 | 42.6 | 2.48 | 9.7 | 25.5 | 20.9 | 22.8 | 26.5 | 2.3 | 1.06 | 2.52 | 1.08 | 220 | 206 | 2424 | 2400
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:05:00 | 4088.16 | 3886.54 | 787292.52 | 759262.26 | 73.7 | 4241.733 | 231.093 | 49.923 | 5 | 176 | 28.5 | 51.6 | 28.8 | 51.1 | 0 | 0 | - | - | 31.8 | 47 | 220 | 206 | 54.8 | 54.5 | 65.8 | 22.3 | 39.5 | 2.28 | 10.6 | 24.5 | 55 | 70.8 | 22.4 | 43.3 | 2.53 | 10.3 | 26.2 | 20.4 | 22.4 | 26.7 | 2.37 | 1.03 | 2.59 | 1.05 | 220 | 206 | 2740 | 2740
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:10:00 | 4093.02 | 3886.54 | 787297.36 | 759262.26 | 74.47 | 4241.733 | 231.093 | 40.07 | 6 | 176 | 28.4 | 51.5 | 28.6 | 51.1 | 0 | 0 | - | - | 31.8 | 47.1 | 220 | 206 | 55.3 | 55.6 | 67 | 21.8 | 40.1 | 2.29 | 10.2 | 25.5 | 55.5 | 71.9 | 21.9 | 43.7 | 2.54 | 10 | 27 | 20 | 21.9 | 27.3 | 2.4 | 1.03 | 2.59 | 1.04 | 220 | 206 | 2722 | 2722
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:15:00 | 4093.68 | 3887.5 | 787297.96 | 759263.22 | 75.25 | 4204.458 | 268.368 | -13.667 | 6 | 176 | 28.3 | 51.4 | 28.5 | 51.1 | 0 | 0 | - | - | 31.7 | 47.2 | 220 | 206 | 55.8 | 55.7 | 67.1 | 21.6 | 40.1 | 2.29 | 10.2 | 25.6 | 56 | 72.3 | 21.7 | 43.8 | 2.55 | 10 | 27.3 | 19.7 | 21.7 | 27.7 | 2.38 | 1.02 | 2.59 | 1.03 | 220 | 206 | 2766 | 2766
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:20:00 | 4093.68 | 3888.76 | 787297.96 | 759264.52 | 76.02 | 4249.188 | 223.638 | 1.617 | 6 | 176 | 28.3 | 51.3 | 28.3 | 51.1 | 0 | 0 | - | - | 31.6 | 47.2 | 220 | 206 | 54.8 | 55.2 | 66.5 | 21.3 | 39.6 | 2.27 | 10 | 25.4 | 55 | 71.8 | 21.3 | 43.4 | 2.52 | 9.8 | 27.3 | 19.4 | 21.4 | 26.9 | 2.36 | 1.02 | 2.57 | 1.03 | 220 | 206 | 2736 | 2736
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:25:00 | 4093.72 | 3890.06 | 787298 | 759265.84 | 76.79 | 4249.188 | 223.638 | -15.445 | 6 | 176 | 28.2 | 51.1 | 28.1 | 51.1 | 0 | 0 | - | - | 31.6 | 47.3 | 220 | 206 | 54.8 | 55.2 | 66.5 | 20.9 | 39.8 | 2.28 | 9.9 | 25.2 | 55 | 71.8 | 21.1 | 43.3 | 2.52 | 9.9 | 27.3 | 19.2 | 21.2 | 26.9 | 2.37 | 1.01 | 2.57 | 1.02 | 220 | 206 | 2760 | 2760
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:30:00 | 4093.72 | 3891.22 | 787298 | 759266.96 | 77.58 | 4204.458 | 268.368 | -12.671 | 6 | 176 | 28.1 | 51 | 28 | 51.1 | 0 | 0 | - | - | 31.5 | 47.3 | 220 | 206 | 55.7 | 55.7 | 66.7 | 20.7 | 39.6 | 2.27 | 9.9 | 25.6 | 55.5 | 72.2 | 20.8 | 43.4 | 2.52 | 9.9 | 27.6 | 18.8 | 20.8 | 26.9 | 2.36 | 1 | 2.58 | 1.01 | 220 | 206 | 2794 | 2794
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:35:00 | 4093.72 | 3892.44 | 787298 | 759268.24 | 78.38 | 4241.733 | 231.093 | -15.799 | 6 | 176 | 28 | 50.9 | 27.9 | 51 | 0 | 0 | - | - | 31.5 | 47.3 | 220 | 206 | 56.7 | 56.7 | 67.4 | 20.4 | 40.1 | 2.29 | 10 | 25.8 | 56.6 | 72.6 | 20.6 | 43.6 | 2.54 | 10 | 27.7 | 18.6 | 20.6 | 27.3 | 2.39 | 0.99 | 2.6 | 1 | 220 | 206 | 2907 | 2901
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:40:00 | 4093.74 | 3893.78 | 787298.02 | 759269.5 | 79.21 | 4249.188 | 223.638 | -17.266 | 6 | 176 | 27.9 | 50.8 | 27.7 | 50.9 | 0 | 0 | - | - | 31.4 | 47.3 | 220 | 206 | 56.7 | 56.7 | 67.5 | 20.1 | 40 | 2.29 | 9.8 | 26 | 56.6 | 73 | 20.2 | 43.7 | 2.54 | 9.9 | 28.1 | 18.2 | 20.2 | 27.2 | 2.39 | 0.99 | 2.6 | 0.99 | 220 | 206 | 2893 | 2893
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:45:00 | 4093.76 | 3895.06 | 787298.04 | 759270.8 | 80.05 | 4249.188 | 223.638 | -14.808 | 6 | 176 | 27.7 | 50.7 | 27.6 | 50.8 | 0 | 0 | - | - | 31.4 | 47.3 | 220 | 206 | 57.6 | 57.7 | 68 | 19.8 | 40.1 | 2.31 | 10.3 | 26.3 | 57.7 | 73.4 | 19.9 | 43.8 | 2.56 | 10 | 28.2 | 17.9 | 19.9 | 27.8 | 2.4 | 0.97 | 2.61 | 0.98 | 220 | 206 | 2955 | 2955
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:50:00 | 4093.76 | 3896.3 | 787298.04 | 759272.08 | 80.89 | 4204.458 | 268.368 | -22.17 | 6 | 176 | 27.6 | 50.6 | 27.4 | 50.8 | 0 | 0 | - | - | 31.3 | 47.3 | 220 | 206 | 57.3 | 57.2 | 67.8 | 19.6 | 40.1 | 2.3 | 9.7 | 26.1 | 57.6 | 73.5 | 19.6 | 43.8 | 2.55 | 9.8 | 28.3 | 17.7 | 19.7 | 27.5 | 2.4 | 0.97 | 2.61 | 0.97 | 220 | 206 | 2973 | 2973
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 21:55:00 | 4093.76 | 3897.54 | 787298.04 | 759273.3 | 81.75 | 4234.278 | 238.548 | -14.883 | 6 | 176 | 27.4 | 50.5 | 27.2 | 50.8 | 0 | 0 | - | - | 31.2 | 47.3 | 220 | 206 | 57.8 | 57.7 | 68 | 19.2 | 39.9 | 2.28 | 10 | 26.6 | 57.6 | 73.5 | 19.3 | 43.7 | 2.54 | 9.8 | 28.6 | 17.3 | 19.3 | 27.6 | 2.39 | 0.96 | 2.6 | 0.96 | 220 | 206 | 3000 | 3000
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:00:00 | 4093.76 | 3898.82 | 787298.04 | 759274.58 | 82.15 | 4204.458 | 268.368 | -15.811 | 6 | 176 | 27.3 | 50.8 | 27 | 51.1 | 0 | 0 | - | - | 31.1 | 47.3 | 0 | 0 | 0 | 0 | 46 | 26.3 | 29.9 | 1.53 | 5.5 | 20.6 | 0 | 49 | 27.1 | 32.6 | 1.67 | 6.1 | 21.2 | 21.2 | 21.3 | 27.3 | 1.53 | 1.39 | 1.63 | 1.39 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:05:00 | 4093.76 | 3900.14 | 787298.04 | 759275.9 | 82.34 | 4249.188 | 223.638 | -17.319 | 6 | 176 | 27.2 | 51.3 | 27 | 51.4 | 0 | 0 | - | - | 31.1 | 47.3 | 0 | 0 | 0 | 0 | 30.7 | 35.9 | 29 | 1.41 | 13.1 | 7.8 | 0 | 29.9 | 40.6 | 29.9 | 1.45 | 17.5 | 6.9 | 22.9 | 22.9 | 26.7 | 1.45 | 1.46 | 1.45 | 1.46 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:10:00 | 4093.76 | 3901.48 | 787298.04 | 759277.26 | 82.53 | 4249.188 | 223.638 | -13.979 | 6 | 176 | 27.1 | 51.6 | 26.9 | 51.7 | 0 | 0 | - | - | 31 | 47.4 | 0 | 0 | 0 | 0 | 30.3 | 34.1 | 28.9 | 1.44 | 10.7 | 7 | 0 | 29.5 | 38.7 | 29.2 | 1.45 | 15.1 | 6.2 | 23.5 | 23.4 | 26.2 | 1.47 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:15:00 | 4093.78 | 3902.78 | 787298.06 | 759278.52 | 82.71 | 4249.188 | 223.638 | -16.342 | 6 | 176 | 27 | 51.8 | 26.9 | 51.8 | 0 | 0 | - | - | 30.9 | 47.4 | 0 | 0 | 0 | 0 | 30.3 | 33.1 | 28.8 | 1.45 | 9.3 | 6.7 | 0 | 29.8 | 36.4 | 28.7 | 1.47 | 12.4 | 6.3 | 23.7 | 23.7 | 26.3 | 1.48 | 1.49 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:20:00 | 4093.8 | 3903.98 | 787298.08 | 759279.72 | 82.88 | 4249.188 | 223.638 | -16.832 | 6 | 176 | 26.9 | 52.1 | 26.8 | 52 | 0 | 0 | - | - | 30.9 | 47.5 | 0 | 0 | 0 | 0 | 30.2 | 32.7 | 28.8 | 1.46 | 8.7 | 6.3 | 0 | 29.8 | 35.1 | 28.3 | 1.47 | 10.9 | 6.1 | 23.9 | 23.9 | 26.6 | 1.49 | 1.5 | 1.49 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:25:00 | 4093.8 | 3905.3 | 787298.08 | 759281.02 | 83.05 | 4219.368 | 253.458 | -17.58 | 6 | 176 | 26.8 | 52.2 | 26.7 | 52.3 | 0 | 0 | - | - | 30.8 | 47.5 | 0 | 0 | 0 | 0 | 29.8 | 32.5 | 28.7 | 1.46 | 8.4 | 5.9 | 0 | 29.7 | 34.1 | 28.1 | 1.48 | 9.9 | 5.9 | 24 | 23.9 | 26.6 | 1.49 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:30:00 | 4093.8 | 3906.56 | 787298.08 | 759282.32 | 83.21 | 4211.913 | 260.913 | -17.588 | 6 | 176 | 26.8 | 52.3 | 26.7 | 52.3 | 0 | 0 | - | - | 30.7 | 47.6 | 0 | 0 | 0 | 0 | 29.6 | 32.4 | 28.6 | 1.47 | 8.3 | 5.5 | 0 | 29.5 | 33.6 | 28.1 | 1.48 | 9.2 | 5.6 | 24.1 | 24 | 27 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:35:00 | 4093.82 | 3907.94 | 787298.1 | 759283.72 | 83.37 | 4249.188 | 223.638 | -16.528 | 6 | 176 | 26.7 | 52.4 | 26.7 | 52.3 | 0 | 0 | - | - | 30.6 | 47.7 | 0 | 0 | 0 | 0 | 29.3 | 32.4 | 28.6 | 1.47 | 8.2 | 5.3 | 0 | 29.3 | 33.2 | 27.9 | 1.48 | 8.8 | 5.4 | 24.1 | 24.1 | 26.7 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:40:00 | 4093.84 | 3909.2 | 787298.12 | 759284.94 | 83.52 | 4249.188 | 223.638 | -15.206 | 6 | 176 | 26.7 | 52.4 | 26.7 | 52.4 | 0 | 0 | - | - | 30.6 | 47.7 | 0 | 0 | 0 | 0 | 29.2 | 32.4 | 28.5 | 1.47 | 8.1 | 5 | 0 | 29.2 | 32.7 | 27.8 | 1.49 | 8.3 | 5.3 | 24.1 | 24.1 | 26.6 | 1.5 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:45:00 | 4093.84 | 3910.58 | 787298.12 | 759286.38 | 83.67 | 4249.188 | 223.638 | -16.846 | 6 | 176 | 26.6 | 52.5 | 26.6 | 52.4 | 0 | 0 | - | - | 30.5 | 47.8 | 0 | 0 | 0 | 0 | 28.8 | 32.7 | 28.4 | 1.47 | 8.4 | 4.6 | 0 | 29.1 | 32.6 | 27.7 | 1.49 | 8.1 | 5 | 24.2 | 24.1 | 26.3 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:50:00 | 4093.86 | 3911.86 | 787298.14 | 759287.58 | 83.81 | 4241.733 | 231.093 | -12.805 | 6 | 176 | 26.5 | 52.6 | 26.6 | 52.5 | 0 | 0 | - | - | 30.4 | 47.8 | 0 | 0 | 0 | 0 | 28.4 | 32.9 | 28.2 | 1.47 | 8.6 | 4.2 | 0 | 28.8 | 32.4 | 27.6 | 1.49 | 7.8 | 4.8 | 24.2 | 24.2 | 26.3 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 22:55:00 | 4093.86 | 3913.32 | 787298.14 | 759289.08 | 83.95 | 4249.188 | 223.638 | -16.194 | 6 | 176 | 26.5 | 52.7 | 26.5 | 52.5 | 0 | 0 | - | - | 30.4 | 47.9 | 0 | 0 | 0 | 0 | 28.2 | 32.9 | 28.1 | 1.47 | 8.6 | 4 | 0 | 28.6 | 32.1 | 27.4 | 1.49 | 7.5 | 4.5 | 24.2 | 24.2 | 26.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:00:00 | 4093.88 | 3914.72 | 787298.16 | 759290.52 | 84.09 | 4249.188 | 223.638 | -18.029 | 6 | 176 | 26.4 | 52.7 | 26.5 | 52.5 | 0 | 0 | - | - | 30.3 | 47.9 | 0 | 0 | 0 | 0 | 28.1 | 32.6 | 27.8 | 1.47 | 8.2 | 3.8 | 0 | 28.3 | 31.7 | 27.3 | 1.49 | 7.2 | 4.2 | 24.2 | 24.2 | 26.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:05:00 | 4093.88 | 3920.06 | 787298.16 | 759295.84 | 84.22 | 4249.188 | 223.638 | -19.208 | 6 | 176 | 26.4 | 52.8 | 26.5 | 52.6 | 0 | 0 | - | - | 30.3 | 47.9 | 0 | 0 | 0 | 0 | 28.1 | 32.1 | 27.7 | 1.47 | 7.7 | 3.8 | 0 | 28.2 | 31.2 | 27.2 | 1.49 | 6.7 | 4.1 | 24.2 | 24.2 | 26.1 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:10:00 | 4093.92 | 3921.72 | 787298.2 | 759297.5 | 84.35 | 4249.188 | 223.638 | -21.281 | 6 | 176 | 26.3 | 52.8 | 26.4 | 52.6 | 0 | 0 | - | - | 30.2 | 48 | 0 | 0 | 0 | 0 | 28 | 31.7 | 27.7 | 1.47 | 7.2 | 3.8 | 0 | 28.1 | 30.8 | 27.2 | 1.49 | 6.3 | 3.9 | 24.2 | 24.2 | 26.1 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:15:00 | 4093.92 | 3923.46 | 787298.2 | 759299.18 | 84.47 | 4249.188 | 223.638 | -21.828 | 6 | 176 | 26.3 | 52.9 | 26.4 | 52.7 | 0 | 0 | - | - | 30.2 | 48.1 | 0 | 0 | 0 | 0 | 28 | 31.3 | 27.7 | 1.47 | 6.9 | 3.8 | 0 | 28 | 30.6 | 27.3 | 1.49 | 6 | 3.9 | 24.3 | 24.2 | 26.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:20:00 | 4093.92 | 3924.82 | 787298.2 | 759300.58 | 84.6 | 4249.188 | 223.638 | -0.418 | 6 | 176 | 26.3 | 52.9 | 26.4 | 52.7 | 0 | 0 | - | - | 30.1 | 48.1 | 0 | 0 | 0 | 0 | 28.1 | 31.2 | 27.7 | 1.48 | 6.7 | 3.8 | 0 | 28 | 30.3 | 27.3 | 1.49 | 5.7 | 3.8 | 24.3 | 24.2 | 26.4 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:25:00 | 4093.96 | 3925.66 | 787298.24 | 759301.42 | 84.72 | 4249.188 | 223.638 | -43.94 | 6 | 176 | 26.2 | 52.9 | 26.4 | 52.7 | 0 | 0 | - | - | 30.1 | 48.1 | 0 | 0 | 0 | 0 | 28.1 | 31 | 27.7 | 1.48 | 6.5 | 3.8 | 0 | 28 | 30.2 | 27.4 | 1.49 | 5.6 | 3.8 | 24.3 | 24.2 | 26.6 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:30:00 | 4094.02 | 3926.46 | 787298.3 | 759302.22 | 84.83 | 4249.188 | 223.638 | -22.536 | 6 | 176 | 26.2 | 53 | 26.4 | 52.7 | 0 | 0 | - | - | 30.1 | 48.1 | 0 | 0 | 0 | 0 | 28.2 | 30.9 | 27.8 | 1.48 | 6.4 | 4 | 0 | 28 | 30.1 | 27.5 | 1.49 | 5.5 | 3.8 | 24.3 | 24.3 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:35:00 | 4094.04 | 3927.3 | 787298.32 | 759303.04 | 84.94 | 4234.278 | 238.548 | -9.884 | 6 | 176 | 26.2 | 53 | 26.4 | 52.7 | 0 | 0 | - | - | 30 | 48.1 | 0 | 0 | 0 | 0 | 28.2 | 30.7 | 27.8 | 1.48 | 6.3 | 3.9 | 0 | 27.9 | 29.9 | 27.6 | 1.49 | 5.3 | 3.8 | 24.3 | 24.2 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:40:00 | 4094.06 | 3928.08 | 787298.34 | 759303.82 | 85.06 | 4249.188 | 223.638 | -9.992 | 6 | 176 | 26.2 | 53.1 | 26.4 | 52.8 | 0 | 0 | - | - | 30 | 48.1 | 0 | 0 | 0 | 0 | 28.2 | 30.6 | 27.7 | 1.48 | 6 | 3.8 | 0 | 27.8 | 29.7 | 27.6 | 1.49 | 5.1 | 3.7 | 24.3 | 24.3 | 26.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:45:00 | 4094.06 | 3928.86 | 787298.34 | 759304.58 | 85.17 | 4249.188 | 223.638 | -10.317 | 6 | 176 | 26.2 | 53.1 | 26.3 | 52.8 | 0 | 0 | - | - | 30 | 48.2 | 0 | 0 | 0 | 0 | 28.3 | 30.4 | 27.7 | 1.48 | 5.9 | 3.9 | 0 | 27.9 | 29.7 | 27.6 | 1.49 | 5 | 3.7 | 24.3 | 24.3 | 26.6 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:50:00 | 4094.16 | 3929.8 | 787298.44 | 759305.52 | 85.28 | 4249.188 | 223.638 | 0.029 | 6 | 176 | 26.2 | 53.1 | 26.3 | 52.8 | 0 | 0 | - | - | 29.9 | 48.2 | 0 | 0 | 0 | 0 | 28.4 | 30.3 | 27.9 | 1.48 | 5.8 | 4 | 0 | 28 | 29.6 | 27.5 | 1.49 | 4.9 | 3.8 | 24.3 | 24.3 | 26.3 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-01 | / | B10-SmartLogger/B10-ESS02 | 2026-06-02 23:55:00 | 4094.16 | 3930.56 | 787298.44 | 759306.28 | 85.39 | 4249.188 | 223.638 | -10.296 | 6 | 176 | 26.1 | 53.1 | 26.3 | 52.8 | 0 | 0 | - | - | 29.9 | 48.2 | 0 | 0 | 0 | 0 | 28.4 | 30.3 | 28.1 | 1.48 | 5.8 | 4 | 0 | 28 | 29.6 | 27.4 | 1.5 | 4.8 | 3.8 | 24.4 | 24.3 | 26.2 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0