## 5 minutes
Time range: | 2026-06-02 00:00:00 - 2026-06-02 23:59:59
Export time: | 2026-06-03 00:17:10
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge energy(kWh) | Total discharge energy(kWh) | Daily auxiliary power consumption(kWh) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge power(kW) | SOC(%) | Equivalent number of cycles | Battery cabin temperature 1(℃) | Battery cabin humidity 1(%) | Battery cabin temperature 2(℃) | Battery cabin humidity 2(%) | CO concentration 1(ppm) | CO concentration 2(ppm) | H2 concentration 1(ppm) | H2 concentration 2(ppm) | Control unit cabin temperature 1(℃) | Control unit cabin humidity 1(%) | Control status of EEV 1(step) | Control status of EEV 2(step) | Running status of outdoor fan 1(%) | Running status of outdoor fan 2(%) | Discharge temperature of compressor 1(℃) | Suction temperature of refrigerant system 1(℃) | Condenser outlet temperature of refrigerant system 1(℃) | Condenser outlet pressure of refrigerant system 1(Mpa) | Suction superheat degree of refrigerant system 1(℃) | Discharge superheat degree of compressor 1(℃) | Running status of outdoor fan 3(%) | Discharge temperature of compressor 2(℃) | Suction temperature of refrigerant system 2(℃) | Condenser outlet temperature of refrigerant system 2(℃) | Condenser outlet pressure of refrigerant system 2(Mpa) | Suction superheat degree of refrigerant system 2(℃) | Discharge superheat degree of compressor 2(℃) | Battery-side supply water temperature(℃) | Battery-side return water temperature(℃) | Air intake temperature(℃) | Discharge pressure of refrigerant system 1(Mpa) | Suction pressure of refrigerant system 1(Mpa) | Discharge pressure of refrigerant system 2(Mpa) | Suction pressure of refrigerant system 2(Mpa) | Running status of EEV 1(step) | Running status of EEV 2(step) | Compressor 1 running status(rpm) | Compressor 2 running status(rpm)
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:00:00 | 0 | 0 | 758641.3 | 730674.44 | 0 | 4214.076 | 214.02 | -9.031 | 5 | 169 | 25.9 | 55.3 | 25.8 | 55.6 | 0 | 0 | - | - | 29.4 | 48.3 | 0 | 0 | 0 | 0 | 28.5 | 31 | 28.3 | 1.46 | 7 | 4.4 | 0 | 28.1 | 30.2 | 28.2 | 1.47 | 6 | 4.3 | 23.9 | 23.7 | 26.9 | 1.5 | 1.5 | 1.49 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:05:00 | 0.02 | 0.72 | 758641.3 | 730675.16 | 0.07 | 4214.076 | 214.02 | -10.74 | 5 | 169 | 25.9 | 55.3 | 25.8 | 55.6 | 0 | 0 | - | - | 29.4 | 48.3 | 0 | 0 | 0 | 0 | 28.4 | 30.9 | 28.2 | 1.47 | 6.9 | 4.3 | 0 | 28 | 30.1 | 28.2 | 1.47 | 5.9 | 4.3 | 23.9 | 23.8 | 26.9 | 1.5 | 1.5 | 1.49 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:10:00 | 0.02 | 1.42 | 758641.3 | 730675.84 | 0.14 | 4221.456 | 206.64 | -9.755 | 5 | 169 | 25.9 | 55.3 | 25.8 | 55.6 | 0 | 0 | - | - | 29.4 | 48.4 | 0 | 0 | 0 | 0 | 28.3 | 30.8 | 28.2 | 1.47 | 6.8 | 4.2 | 0 | 27.9 | 29.9 | 28.2 | 1.47 | 5.8 | 4.2 | 23.9 | 23.8 | 26.9 | 1.5 | 1.5 | 1.49 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:15:00 | 0.02 | 2.1 | 758641.3 | 730676.54 | 0.21 | 4250.976 | 177.12 | -9.244 | 5 | 169 | 25.9 | 55.4 | 25.8 | 55.6 | 0 | 0 | - | - | 29.3 | 48.4 | 0 | 0 | 0 | 0 | 28.4 | 30.8 | 28.3 | 1.47 | 6.8 | 4.3 | 0 | 28 | 29.9 | 28.2 | 1.47 | 5.8 | 4.2 | 23.9 | 23.8 | 27.1 | 1.5 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:20:00 | 0.02 | 2.72 | 758641.3 | 730677.2 | 0.28 | 4221.456 | 206.64 | -9.898 | 5 | 169 | 25.9 | 55.4 | 25.8 | 55.6 | 0 | 0 | - | - | 29.3 | 48.4 | 0 | 0 | 0 | 0 | 28.6 | 30.9 | 28.6 | 1.47 | 6.9 | 4.5 | 0 | 28.1 | 30 | 28.2 | 1.47 | 5.8 | 4.4 | 24 | 23.8 | 27.2 | 1.5 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:25:00 | 0.14 | 3.74 | 758641.42 | 730678.16 | 0.35 | 4221.456 | 206.64 | -8.8 | 5 | 169 | 25.9 | 55.4 | 25.8 | 55.6 | 0 | 0 | - | - | 29.3 | 48.4 | 0 | 0 | 0 | 0 | 28.7 | 30.9 | 28.7 | 1.47 | 6.9 | 4.5 | 0 | 28.2 | 30.1 | 28.3 | 1.47 | 5.9 | 4.4 | 24 | 23.8 | 27.2 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:30:00 | 0.16 | 4.58 | 758641.44 | 730679.02 | 0.42 | 4250.976 | 177.12 | -8.198 | 5 | 169 | 25.9 | 55.4 | 25.8 | 55.6 | 0 | 0 | - | - | 29.3 | 48.4 | 0 | 0 | 0 | 0 | 28.7 | 30.9 | 28.7 | 1.47 | 6.8 | 4.5 | 0 | 28.2 | 30.1 | 28.3 | 1.48 | 5.8 | 4.4 | 24 | 23.8 | 27.1 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:35:00 | 0.16 | 5.4 | 758641.44 | 730679.84 | 0.49 | 4250.976 | 177.12 | -12.633 | 5 | 169 | 25.9 | 55.4 | 25.8 | 55.6 | 0 | 0 | - | - | 29.3 | 48.4 | 0 | 0 | 0 | 0 | 28.6 | 30.7 | 28.6 | 1.47 | 6.7 | 4.4 | 0 | 28.2 | 29.9 | 28.4 | 1.48 | 5.7 | 4.3 | 24 | 23.8 | 26.8 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:40:00 | 0.22 | 6.26 | 758641.5 | 730680.68 | 0.56 | 4243.596 | 184.5 | -10.176 | 4 | 169 | 25.9 | 55.4 | 25.8 | 55.6 | 0 | 0 | - | - | 29.2 | 48.5 | 0 | 0 | 0 | 0 | 28.4 | 30.7 | 28.3 | 1.47 | 6.5 | 4.2 | 0 | 28 | 29.8 | 28.3 | 1.48 | 5.5 | 4.2 | 24 | 23.8 | 26.7 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:45:00 | 0.24 | 6.96 | 758641.52 | 730681.38 | 0.63 | 4250.976 | 177.12 | -12.178 | 4 | 169 | 25.8 | 55.4 | 25.8 | 55.6 | 0 | 0 | - | - | 29.2 | 48.5 | 0 | 0 | 0 | 0 | 28.4 | 30.6 | 28.2 | 1.47 | 6.4 | 4.2 | 0 | 27.9 | 29.7 | 28.2 | 1.48 | 5.4 | 4.1 | 24 | 23.9 | 26.8 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:50:00 | 0.26 | 7.86 | 758641.54 | 730682.3 | 0.7 | 4258.356 | 169.74 | -10.534 | 4 | 169 | 25.9 | 55.5 | 25.8 | 55.7 | 0 | 0 | - | - | 29.2 | 48.5 | 0 | 0 | 0 | 0 | 28.4 | 30.4 | 28.4 | 1.47 | 6.3 | 4.2 | 0 | 27.9 | 29.7 | 28.3 | 1.48 | 5.4 | 4.1 | 24.1 | 23.9 | 27 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 00:55:00 | 0.3 | 8.64 | 758641.58 | 730683.08 | 0.77 | 4258.356 | 169.74 | -11.542 | 4 | 169 | 25.8 | 55.5 | 25.7 | 55.8 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.5 | 30.5 | 28.6 | 1.47 | 6.3 | 4.3 | 0 | 28 | 29.7 | 28.3 | 1.48 | 5.3 | 4.2 | 24.1 | 23.9 | 27.1 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:00:00 | 0.32 | 9.36 | 758641.6 | 730683.82 | 0.84 | 4258.356 | 169.74 | -11.354 | 4 | 169 | 25.8 | 55.5 | 25.7 | 55.9 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.6 | 30.4 | 28.6 | 1.47 | 6.3 | 4.4 | 0 | 28.1 | 29.7 | 28.4 | 1.48 | 5.3 | 4.2 | 24.1 | 23.9 | 27 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:05:00 | 0.38 | 10.14 | 758641.66 | 730684.56 | 0.91 | 4258.356 | 169.74 | -10.155 | 4 | 169 | 25.8 | 55.5 | 25.8 | 55.7 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.7 | 30.4 | 28.7 | 1.47 | 6.3 | 4.4 | 0 | 28.1 | 29.7 | 28.4 | 1.48 | 5.3 | 4.2 | 24.1 | 23.9 | 27 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:10:00 | 0.42 | 10.96 | 758641.7 | 730685.38 | 0.98 | 4250.976 | 177.12 | -12.928 | 4 | 169 | 25.9 | 55.5 | 25.8 | 55.7 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.8 | 30.4 | 28.9 | 1.47 | 6.2 | 4.5 | 0 | 28.2 | 29.7 | 28.4 | 1.48 | 5.3 | 4.2 | 24.1 | 23.9 | 27 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:15:00 | 0.42 | 11.88 | 758641.7 | 730686.3 | 1.05 | 4258.356 | 169.74 | -8.641 | 4 | 169 | 25.9 | 55.5 | 25.9 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.8 | 30.3 | 28.8 | 1.47 | 6.2 | 4.5 | 0 | 28.2 | 29.7 | 28.5 | 1.48 | 5.3 | 4.2 | 24.1 | 23.9 | 27 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:20:00 | 0.48 | 12.5 | 758641.76 | 730686.98 | 1.12 | 4258.356 | 169.74 | -12.741 | 4 | 169 | 25.9 | 55.5 | 25.9 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.8 | 30.2 | 28.7 | 1.47 | 6.1 | 4.6 | 0 | 28.2 | 29.6 | 28.5 | 1.48 | 5.2 | 4.2 | 24.1 | 23.9 | 27 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:25:00 | 0.56 | 13.52 | 758641.84 | 730687.94 | 1.19 | 4258.356 | 169.74 | -10.64 | 4 | 169 | 25.9 | 55.4 | 25.9 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.8 | 30.2 | 28.8 | 1.47 | 6.1 | 4.5 | 0 | 28.2 | 29.6 | 28.6 | 1.48 | 5.2 | 4.2 | 24.1 | 24 | 27.2 | 1.51 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:30:00 | 0.58 | 14.32 | 758641.86 | 730688.76 | 1.26 | 4258.356 | 169.74 | -9.216 | 4 | 169 | 25.9 | 55.4 | 25.9 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 29 | 30.2 | 28.9 | 1.47 | 6 | 4.7 | 0 | 28.3 | 29.6 | 28.7 | 1.48 | 5.2 | 4.3 | 24.1 | 24 | 27.1 | 1.51 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:35:00 | 0.66 | 15.16 | 758641.94 | 730689.58 | 1.33 | 4265.736 | 162.36 | -10.348 | 4 | 169 | 25.9 | 55.4 | 25.9 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 29.1 | 30.2 | 29.2 | 1.47 | 6 | 4.9 | 0 | 28.3 | 29.6 | 28.7 | 1.48 | 5.2 | 4.4 | 24.2 | 24 | 27.1 | 1.51 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:40:00 | 0.72 | 15.94 | 758642 | 730690.4 | 1.4 | 4250.976 | 177.12 | -8.364 | 4 | 169 | 25.9 | 55.4 | 25.9 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 29.2 | 30.2 | 29.2 | 1.47 | 5.9 | 4.9 | 0 | 28.4 | 29.6 | 28.8 | 1.48 | 5.2 | 4.4 | 24.2 | 24 | 27.1 | 1.51 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:45:00 | 0.74 | 16.78 | 758642.02 | 730691.2 | 1.47 | 4265.736 | 162.36 | -9.488 | 4 | 169 | 25.9 | 55.5 | 25.9 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 29.3 | 30.2 | 29.3 | 1.48 | 5.9 | 5 | 0 | 28.4 | 29.6 | 28.9 | 1.48 | 5.1 | 4.4 | 24.2 | 24 | 27.1 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:50:00 | 0.78 | 17.54 | 758642.06 | 730691.98 | 1.58 | 4250.976 | 177.12 | -10.405 | 4 | 169 | 25.9 | 55.4 | 25.9 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | -59.7 | -60.1 | 29.2 | 30.1 | 29.2 | 1.48 | 5.8 | 4.7 | -59.8 | 28.3 | 29.6 | 28.9 | 1.49 | 5.1 | 4.3 | 24.2 | 24 | 26.7 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 01:55:00 | 0.8 | 18.4 | 758642.08 | 730692.82 | 1.66 | 4273.116 | 154.98 | -9.412 | 4 | 169 | 25.9 | 55.4 | 26 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.7 | 29.7 | 29.1 | 1.48 | 5.4 | 4.3 | 0 | 28 | 29.7 | 28.7 | 1.49 | 5.2 | 4 | 24.2 | 24 | 26.8 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:00:00 | 0.82 | 19.2 | 758642.1 | 730693.66 | 1.72 | 4273.116 | 154.98 | -6.939 | 4 | 169 | 25.9 | 55.4 | 25.9 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.7 | 29.6 | 29.3 | 1.47 | 5.4 | 4.4 | 0 | 28 | 29.7 | 28.8 | 1.48 | 5.1 | 4 | 24.2 | 24 | 26.7 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:05:00 | 0.88 | 20.02 | 758642.16 | 730694.46 | 1.79 | 4273.116 | 154.98 | -12.294 | 4 | 169 | 25.9 | 55.5 | 26 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 28.9 | 29.6 | 29.4 | 1.47 | 5.4 | 4.6 | 0 | 28.1 | 29.7 | 28.8 | 1.49 | 5.1 | 4 | 24.2 | 24 | 26.8 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:10:00 | 0.88 | 20.72 | 758642.16 | 730695.16 | 1.86 | 4250.976 | 177.12 | -10.348 | 4 | 169 | 25.9 | 55.5 | 26 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 29.1 | 29.6 | 29.5 | 1.47 | 5.4 | 4.9 | 0 | 28.2 | 29.6 | 28.8 | 1.49 | 5.1 | 4.1 | 24.2 | 24.1 | 27 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:15:00 | 0.92 | 21.48 | 758642.2 | 730695.9 | 1.93 | 4280.496 | 147.6 | -9.223 | 4 | 169 | 25.9 | 55.5 | 26 | 55.6 | 0 | 0 | - | - | 29.2 | 48.7 | 0 | 0 | 0 | 0 | 29.2 | 29.4 | 29.5 | 1.47 | 5.4 | 5.1 | 0 | 28.3 | 29.6 | 28.9 | 1.49 | 5.1 | 4.2 | 24.3 | 24.1 | 27 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:20:00 | 1 | 22.26 | 758642.32 | 730696.68 | 2 | 4280.496 | 147.6 | -7.988 | 4 | 169 | 26 | 55.5 | 26 | 55.6 | 0 | 0 | - | - | 29.2 | 48.7 | 0 | 0 | 0 | 0 | 29.3 | 29.4 | 29.6 | 1.47 | 5.4 | 5.2 | 0 | 28.4 | 29.6 | 29 | 1.49 | 5 | 4.3 | 24.3 | 24.1 | 26.8 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:25:00 | 1.04 | 23.02 | 758642.32 | 730697.44 | 2.07 | 4250.976 | 177.12 | -8.314 | 4 | 169 | 26 | 55.5 | 26 | 55.6 | 0 | 0 | - | - | 29.2 | 48.6 | 0 | 0 | 0 | 0 | 29.5 | 29.3 | 29.7 | 1.47 | 5.3 | 5.4 | 0 | 28.5 | 29.6 | 29.1 | 1.49 | 5 | 4.4 | 24.3 | 24.1 | 27 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:30:00 | 1.04 | 23.6 | 758642.32 | 730698.04 | 2.14 | 4250.976 | 177.12 | -9.959 | 4 | 169 | 25.9 | 55.5 | 25.9 | 55.7 | 0 | 0 | - | - | 29.2 | 48.7 | 0 | 0 | 0 | 0 | 29.6 | 29.3 | 29.9 | 1.47 | 5.4 | 5.5 | 0 | 28.5 | 29.6 | 29.2 | 1.49 | 5.1 | 4.4 | 24.3 | 24.1 | 27.1 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:35:00 | 1.04 | 24.2 | 758642.32 | 730698.66 | 2.21 | 4250.976 | 177.12 | -8.591 | 4 | 169 | 25.9 | 55.5 | 25.9 | 55.8 | 0 | 0 | - | - | 29.2 | 48.7 | 0 | 0 | 0 | 0 | 29.7 | 29.3 | 30.1 | 1.47 | 5.3 | 5.6 | 0 | 28.6 | 29.6 | 29.3 | 1.49 | 5 | 4.5 | 24.3 | 24.2 | 27.1 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:40:00 | 1.04 | 24.8 | 758642.32 | 730699.26 | 2.28 | 4250.976 | 177.12 | -7.71 | 4 | 169 | 25.9 | 55.5 | 25.9 | 55.7 | 0 | 0 | - | - | 29.2 | 48.7 | 0 | 0 | 0 | 0 | 29.7 | 29.3 | 29.8 | 1.47 | 5.3 | 5.5 | 0 | 28.6 | 29.6 | 29.4 | 1.49 | 5 | 4.4 | 24.3 | 24.2 | 27.1 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:45:00 | 1.04 | 25.44 | 758642.32 | 730699.86 | 2.35 | 4250.976 | 177.12 | -10.395 | 4 | 169 | 25.9 | 55.5 | 26 | 55.7 | 0 | 0 | - | - | 29.2 | 48.7 | 0 | 0 | 0 | 0 | 29.3 | 29.2 | 29.6 | 1.47 | 5.1 | 5.2 | 0 | 28.4 | 29.4 | 29.4 | 1.49 | 4.9 | 4.3 | 24.4 | 24.2 | 26.9 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:50:00 | 1.1 | 26.12 | 758642.38 | 730700.54 | 2.42 | 4250.976 | 177.12 | -9.188 | 4 | 169 | 25.9 | 55.5 | 26 | 55.6 | 0 | 0 | - | - | 29.2 | 48.7 | 0 | 0 | 0 | 0 | 29.2 | 29.1 | 29.2 | 1.47 | 5 | 5 | 0 | 28.3 | 29.3 | 29.3 | 1.49 | 4.7 | 4.2 | 24.3 | 24.2 | 26.9 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 02:55:00 | 1.12 | 26.8 | 758642.4 | 730701.22 | 2.49 | 4295.256 | 132.84 | 6.94 | 4 | 169 | 26 | 55.5 | 26 | 55.6 | 0 | 0 | - | - | 29.2 | 48.8 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 29.2 | 1.47 | 4.9 | 4.9 | 0 | 28.2 | 29.2 | 29.2 | 1.49 | 4.6 | 4.1 | 24.4 | 24.2 | 26.9 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:00:00 | 1.2 | 27.46 | 758642.48 | 730701.88 | 2.56 | 4250.976 | 177.12 | -10.867 | 4 | 169 | 26 | 55.5 | 26 | 55.7 | 0 | 0 | - | - | 29.2 | 48.7 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 29.2 | 1.47 | 4.9 | 4.9 | 0 | 28.2 | 29.2 | 29.2 | 1.49 | 4.6 | 4.1 | 24.4 | 24.2 | 26.9 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:05:00 | 1.2 | 27.96 | 758642.48 | 730702.4 | 2.63 | 4250.976 | 177.12 | -10.666 | 4 | 169 | 26 | 55.6 | 26 | 55.7 | 0 | 0 | - | - | 29.2 | 48.8 | 0 | 0 | 0 | 0 | 29.2 | 29 | 29.4 | 1.47 | 4.9 | 5.1 | 0 | 28.4 | 29.1 | 29.2 | 1.49 | 4.6 | 4.3 | 24.4 | 24.2 | 26.9 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:10:00 | 1.2 | 28.6 | 758642.48 | 730703.02 | 2.7 | 4250.976 | 177.12 | -8.998 | 4 | 169 | 25.9 | 55.6 | 26 | 55.7 | 0 | 0 | - | - | 29.2 | 48.8 | 0 | 0 | 0 | 0 | 29.4 | 29 | 29.6 | 1.46 | 5 | 5.3 | 0 | 28.4 | 29.1 | 29.3 | 1.49 | 4.6 | 4.4 | 24.4 | 24.2 | 27.1 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:15:00 | 1.2 | 29.2 | 758642.48 | 730703.64 | 2.77 | 4250.976 | 177.12 | -10.375 | 4 | 169 | 25.9 | 55.6 | 26 | 55.6 | 0 | 0 | - | - | 29.2 | 48.8 | 0 | 0 | 0 | 0 | 29.4 | 29 | 29.6 | 1.46 | 5 | 5.3 | 0 | 28.5 | 29.1 | 29.3 | 1.49 | 4.5 | 4.4 | 24.4 | 24.2 | 27.1 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:20:00 | 1.2 | 29.82 | 758642.48 | 730704.24 | 2.84 | 4250.976 | 177.12 | -7.721 | 4 | 169 | 26 | 55.6 | 26.1 | 55.7 | 0 | 0 | - | - | 29.2 | 48.8 | 0 | 0 | 0 | 0 | 29.5 | 29 | 29.6 | 1.47 | 4.9 | 5.4 | 0 | 28.6 | 29.1 | 29.3 | 1.49 | 4.6 | 4.5 | 24.4 | 24.3 | 27.2 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:25:00 | 1.22 | 30.26 | 758642.5 | 730704.68 | 2.91 | 4250.976 | 177.12 | -31.194 | 4 | 169 | 26 | 55.6 | 26.1 | 55.6 | 0 | 0 | - | - | 29.2 | 48.9 | 0 | 0 | 0 | 0 | 29.5 | 29 | 29.6 | 1.47 | 4.9 | 5.3 | 0 | 28.6 | 29.1 | 29.3 | 1.49 | 4.5 | 4.5 | 24.4 | 24.3 | 27.2 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:30:00 | 1.34 | 31.02 | 758642.62 | 730705.46 | 2.98 | 4287.876 | 140.22 | -9.354 | 4 | 169 | 26 | 55.6 | 26.1 | 55.6 | 0 | 0 | - | - | 29.1 | 48.9 | 0 | 0 | 0 | 0 | 29.6 | 29.1 | 29.4 | 1.47 | 4.9 | 5.3 | 0 | 28.6 | 29.1 | 29.3 | 1.48 | 4.6 | 4.5 | 24.5 | 24.3 | 27.2 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:35:00 | 1.34 | 31.7 | 758642.62 | 730706.12 | 3.05 | 4258.356 | 169.74 | -8.161 | 4 | 169 | 26 | 55.6 | 26.1 | 55.6 | 0 | 0 | - | - | 29.1 | 48.9 | 0 | 0 | 0 | 0 | 29.3 | 28.9 | 29.2 | 1.47 | 4.8 | 5.1 | 0 | 28.4 | 28.9 | 29.3 | 1.48 | 4.5 | 4.5 | 24.4 | 24.2 | 27.1 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:40:00 | 1.4 | 32.32 | 758642.68 | 730706.8 | 3.12 | 4258.356 | 169.74 | -9.996 | 4 | 169 | 26 | 55.6 | 26.1 | 55.6 | 0 | 0 | - | - | 29.1 | 48.9 | 0 | 0 | 0 | 0 | 29.3 | 28.9 | 29.2 | 1.47 | 4.8 | 5.1 | 0 | 28.4 | 28.9 | 29.3 | 1.48 | 4.5 | 4.5 | 24.5 | 24.3 | 27.1 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:45:00 | 1.4 | 32.94 | 758642.68 | 730707.38 | 3.19 | 4258.356 | 169.74 | -9.924 | 4 | 169 | 26 | 55.6 | 26.1 | 55.6 | 0 | 0 | - | - | 29.1 | 49 | 0 | 0 | 0 | 0 | 29.1 | 28.8 | 29.1 | 1.47 | 4.7 | 4.8 | 0 | 28.3 | 28.8 | 29.3 | 1.48 | 4.4 | 4.3 | 24.5 | 24.3 | 27.1 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:50:00 | 1.4 | 33.68 | 758642.68 | 730708.1 | 3.26 | 4258.356 | 169.74 | -8.851 | 4 | 169 | 26 | 55.6 | 26.1 | 55.7 | 0 | 0 | - | - | 29.1 | 49 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.9 | 1.47 | 4.6 | 4.7 | 0 | 28.2 | 28.7 | 29.2 | 1.48 | 4.3 | 4.2 | 24.5 | 24.3 | 27.1 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 03:55:00 | 1.44 | 34.34 | 758642.72 | 730708.78 | 3.32 | 4287.876 | 140.22 | -6.908 | 4 | 169 | 26 | 55.6 | 26.1 | 55.7 | 0 | 0 | - | - | 29.1 | 49.1 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.9 | 1.47 | 4.5 | 4.6 | 0 | 28.2 | 28.7 | 29.2 | 1.48 | 4.2 | 4.2 | 24.5 | 24.3 | 27.1 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:00:00 | 1.44 | 34.98 | 758642.72 | 730709.44 | 3.39 | 4265.736 | 162.36 | -10.412 | 4 | 169 | 26 | 55.7 | 26.1 | 55.7 | 0 | 0 | - | - | 29.1 | 49.1 | 0 | 0 | 0 | 0 | 28.8 | 28.6 | 28.9 | 1.47 | 4.4 | 4.5 | 0 | 28.2 | 28.6 | 29.2 | 1.48 | 4.1 | 4.2 | 24.5 | 24.3 | 27.4 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:05:00 | 1.44 | 35.66 | 758642.72 | 730710.08 | 3.46 | 4265.736 | 162.36 | -9.043 | 4 | 169 | 26 | 55.7 | 26.1 | 55.7 | 0 | 0 | - | - | 29.1 | 49.2 | 0 | 0 | 0 | 0 | 28.9 | 28.6 | 29 | 1.47 | 4.5 | 4.7 | 0 | 28.2 | 28.6 | 29.2 | 1.49 | 4.1 | 4.2 | 24.6 | 24.4 | 27.4 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:10:00 | 1.46 | 36.44 | 758642.74 | 730710.88 | 3.53 | 4295.256 | 132.84 | -4.476 | 4 | 169 | 26 | 55.7 | 26.1 | 55.7 | 0 | 0 | - | - | 29 | 49.2 | 0 | 0 | 0 | 0 | 29 | 28.7 | 29 | 1.47 | 4.5 | 4.8 | 0 | 28.3 | 28.4 | 29.1 | 1.48 | 4 | 4.3 | 24.6 | 24.4 | 27.3 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:15:00 | 1.52 | 37.04 | 758642.8 | 730711.48 | 3.6 | 4287.876 | 140.22 | -47.332 | 4 | 169 | 26 | 55.7 | 26.1 | 55.7 | 0 | 0 | - | - | 29 | 49.2 | 0 | 0 | 0 | 0 | 29.1 | 28.7 | 29 | 1.47 | 4.6 | 4.9 | 0 | 28.3 | 28.4 | 29.1 | 1.48 | 4 | 4.3 | 24.6 | 24.4 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:20:00 | 1.52 | 37.74 | 758642.8 | 730712.18 | 3.67 | 4265.736 | 162.36 | -9.339 | 4 | 169 | 26 | 55.7 | 26.1 | 55.7 | 0 | 0 | - | - | 29.1 | 49.2 | 0 | 0 | 0 | 0 | 29.1 | 28.7 | 29 | 1.47 | 4.5 | 4.8 | 0 | 28.3 | 28.3 | 29.1 | 1.48 | 3.9 | 4.2 | 24.6 | 24.4 | 27.4 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:25:00 | 1.52 | 38.34 | 758642.8 | 730712.78 | 3.74 | 4265.736 | 162.36 | -11.498 | 4 | 169 | 26 | 55.7 | 26.1 | 55.7 | 0 | 0 | - | - | 29 | 49.3 | 0 | 0 | 0 | 0 | 29.1 | 28.7 | 29 | 1.47 | 4.5 | 4.9 | 0 | 28.3 | 28.3 | 29.1 | 1.48 | 3.9 | 4.3 | 24.6 | 24.4 | 27.4 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:30:00 | 1.52 | 38.9 | 758642.8 | 730713.32 | 3.81 | 4265.736 | 162.36 | -12.472 | 4 | 169 | 26 | 55.7 | 26.1 | 55.7 | 0 | 0 | - | - | 29 | 49.3 | 0 | 0 | 0 | 0 | 29.3 | 28.9 | 29.1 | 1.47 | 4.6 | 5 | 0 | 28.4 | 28.4 | 29.1 | 1.48 | 3.9 | 4.4 | 24.6 | 24.4 | 27.3 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:35:00 | 1.52 | 39.62 | 758642.8 | 730714.04 | 3.88 | 4295.256 | 132.84 | -9.581 | 4 | 169 | 26.1 | 55.8 | 26.1 | 55.7 | 0 | 0 | - | - | 29 | 49.4 | 0 | 0 | 0 | 0 | 29.4 | 28.9 | 29.3 | 1.47 | 4.7 | 5.1 | 0 | 28.5 | 28.4 | 29.2 | 1.48 | 4 | 4.5 | 24.6 | 24.4 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:40:00 | 1.58 | 40.3 | 758642.86 | 730714.74 | 3.95 | 4273.116 | 154.98 | -0.62 | 4 | 169 | 26 | 55.7 | 26.1 | 55.7 | 0 | 0 | - | - | 29 | 49.3 | 0 | 0 | 0 | 0 | 29.3 | 28.8 | 29.2 | 1.47 | 4.6 | 5.1 | 0 | 28.4 | 28.4 | 29.2 | 1.49 | 3.9 | 4.4 | 24.6 | 24.4 | 27.1 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:45:00 | 1.62 | 41.02 | 758642.9 | 730715.44 | 4.02 | 4273.116 | 154.98 | -9.717 | 4 | 169 | 26.1 | 55.7 | 26.1 | 55.7 | 0 | 0 | - | - | 29.1 | 49.3 | 0 | 0 | 0 | 0 | 29.2 | 28.8 | 29.1 | 1.47 | 4.6 | 4.9 | 0 | 28.3 | 28.4 | 29.2 | 1.48 | 3.9 | 4.3 | 24.6 | 24.4 | 27.1 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:50:00 | 1.62 | 41.64 | 758642.9 | 730716.06 | 4.09 | 4280.496 | 147.6 | -3.944 | 3 | 169 | 26.1 | 55.7 | 26.2 | 55.7 | 0 | 0 | - | - | 29.1 | 49.4 | 0 | 0 | 0 | 0 | 29.1 | 28.7 | 28.9 | 1.47 | 4.5 | 4.7 | 0 | 28.2 | 28.2 | 29.2 | 1.49 | 3.8 | 4.2 | 24.7 | 24.5 | 27.1 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 04:55:00 | 1.96 | 42.12 | 758643.26 | 730716.56 | 4.16 | 4280.496 | 147.6 | -3.078 | 3 | 169 | 26.1 | 55.8 | 26.2 | 55.7 | 0 | 0 | - | - | 29.1 | 49.3 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.8 | 1.47 | 4.4 | 4.5 | 0 | 28.2 | 28.2 | 29.1 | 1.48 | 3.7 | 4.1 | 24.7 | 24.5 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:00:00 | 2.32 | 42.64 | 758643.62 | 730717.08 | 4.23 | 4287.876 | 140.22 | -4.301 | 3 | 169 | 26 | 55.8 | 26.1 | 55.8 | 0 | 0 | - | - | 29 | 49.4 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.9 | 1.47 | 4.4 | 4.5 | 0 | 28.2 | 28.2 | 29.1 | 1.49 | 3.6 | 4.1 | 24.7 | 24.5 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:05:00 | 2.72 | 43.28 | 758644 | 730717.7 | 4.3 | 4295.256 | 132.84 | 22.849 | 3 | 169 | 26 | 55.8 | 26 | 55.9 | 0 | 0 | - | - | 29 | 49.4 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.9 | 1.47 | 4.3 | 4.5 | 0 | 28.2 | 28.2 | 29.1 | 1.49 | 3.6 | 4.1 | 24.7 | 24.5 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:10:00 | 3.22 | 43.8 | 758644.54 | 730718.26 | 4.37 | 4295.256 | 132.84 | 1.482 | 3 | 169 | 26 | 55.8 | 26 | 56 | 0 | 0 | - | - | 29 | 49.4 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.9 | 1.48 | 4.3 | 4.4 | 0 | 28.2 | 28.1 | 29.1 | 1.49 | 3.6 | 4 | 24.7 | 24.5 | 27.3 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:15:00 | 3.96 | 44.32 | 758645.24 | 730718.74 | 4.44 | 4295.256 | 132.84 | 3.458 | 3 | 169 | 26 | 55.9 | 26.1 | 55.9 | 0 | 0 | - | - | 29 | 49.5 | 0 | 0 | 0 | 0 | 28.7 | 28.7 | 28.8 | 1.47 | 4.4 | 4.4 | 0 | 28.1 | 28.1 | 29.1 | 1.49 | 3.5 | 4 | 24.7 | 24.5 | 27.3 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:20:00 | 4.68 | 44.8 | 758645.96 | 730719.24 | 4.51 | 4295.256 | 132.84 | 7.291 | 3 | 169 | 26 | 55.9 | 26.2 | 55.8 | 0 | 0 | - | - | 29 | 49.5 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.9 | 1.47 | 4.4 | 4.6 | 0 | 28.2 | 28.1 | 29.1 | 1.49 | 3.5 | 4.2 | 24.7 | 24.5 | 27.1 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:25:00 | 5.46 | 45.24 | 758646.76 | 730719.66 | 4.58 | 4295.256 | 132.84 | 2.2 | 3 | 169 | 26 | 55.9 | 26.2 | 55.8 | 0 | 0 | - | - | 28.9 | 49.6 | 0 | 0 | 0 | 0 | 29 | 28.7 | 28.8 | 1.47 | 4.5 | 4.6 | 0 | 28.2 | 28.1 | 29 | 1.49 | 3.5 | 4.2 | 24.7 | 24.6 | 27.1 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:30:00 | 6.2 | 45.62 | 758647.48 | 730720.1 | 4.64 | 4295.256 | 132.84 | -0.386 | 3 | 169 | 26 | 55.9 | 26.2 | 55.8 | 0 | 0 | - | - | 28.9 | 49.6 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.8 | 1.47 | 4.4 | 4.6 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.5 | 4.1 | 24.7 | 24.6 | 27.1 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:35:00 | 6.98 | 46.1 | 758648.26 | 730720.56 | 4.71 | 4295.256 | 132.84 | 5.2 | 3 | 169 | 26 | 55.9 | 26.2 | 55.8 | 0 | 0 | - | - | 28.9 | 49.6 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.8 | 1.47 | 4.4 | 4.5 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.5 | 4.1 | 24.7 | 24.6 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:40:00 | 7.72 | 46.52 | 758649 | 730720.96 | 4.78 | 4295.256 | 132.84 | 1.425 | 3 | 169 | 26 | 55.9 | 26.2 | 55.9 | 0 | 0 | - | - | 28.9 | 49.7 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.7 | 1.48 | 4.4 | 4.6 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.4 | 4.1 | 24.7 | 24.6 | 27.1 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:45:00 | 8.4 | 46.9 | 758649.72 | 730721.34 | 4.85 | 4295.256 | 132.84 | 2.302 | 3 | 169 | 26 | 55.9 | 26.2 | 55.8 | 0 | 0 | - | - | 28.9 | 49.7 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.7 | 1.48 | 4.5 | 4.6 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.4 | 4.1 | 24.8 | 24.6 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:50:00 | 9.14 | 47.3 | 758650.44 | 730721.72 | 4.92 | 4295.256 | 132.84 | -1.705 | 3 | 169 | 26 | 55.9 | 26.2 | 55.8 | 0 | 0 | - | - | 28.9 | 49.7 | 0 | 0 | 0 | 0 | 29 | 28.8 | 28.8 | 1.48 | 4.5 | 4.6 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.5 | 4.1 | 24.7 | 24.6 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 05:55:00 | 9.94 | 47.72 | 758651.24 | 730722.16 | 4.99 | 4295.256 | 132.84 | 14.354 | 3 | 169 | 26.1 | 55.9 | 26.2 | 55.8 | 0 | 0 | - | - | 28.9 | 49.7 | 0 | 0 | 0 | 0 | 29 | 28.8 | 28.8 | 1.48 | 4.5 | 4.6 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.5 | 4.1 | 24.8 | 24.6 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:00:00 | 10.98 | 47.98 | 758652.28 | 730722.4 | 5.06 | 4295.256 | 132.84 | 10.134 | 3 | 169 | 26 | 56 | 26.2 | 55.9 | 0 | 0 | - | - | 28.9 | 49.7 | 0 | 0 | 0 | 0 | 29 | 28.8 | 28.8 | 1.48 | 4.5 | 4.6 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.5 | 4.1 | 24.8 | 24.6 | 27.2 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:05:00 | 12.48 | 48.04 | 758653.76 | 730722.46 | 5.13 | 4295.256 | 132.84 | 20.128 | 3 | 169 | 26 | 56 | 26.2 | 55.9 | 0 | 0 | - | - | 28.9 | 49.7 | 0 | 0 | 0 | 0 | 29 | 28.8 | 28.8 | 1.48 | 4.5 | 4.6 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.4 | 4.1 | 24.8 | 24.6 | 27.3 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:10:00 | 15.44 | 48.04 | 758656.76 | 730722.46 | 5.2 | 4295.256 | 132.84 | 9.909 | 3 | 169 | 26 | 56 | 26.2 | 55.8 | 0 | 0 | - | - | 29 | 49.7 | 0 | 0 | 0 | 0 | 29.1 | 28.8 | 28.8 | 1.48 | 4.5 | 4.6 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.4 | 4.1 | 24.8 | 24.6 | 27.3 | 1.52 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:15:00 | 16.26 | 48.5 | 758657.54 | 730722.92 | 5.27 | 4295.256 | 132.84 | -19.728 | 3 | 169 | 26 | 56 | 26.2 | 55.9 | 0 | 0 | - | - | 28.9 | 49.8 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 28.8 | 1.48 | 4.5 | 4.6 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.5 | 4.1 | 24.8 | 24.6 | 27.3 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:20:00 | 16.78 | 49.04 | 758658.08 | 730723.48 | 5.34 | 4295.256 | 132.84 | -20.136 | 3 | 169 | 26.1 | 56 | 26.2 | 55.8 | 0 | 0 | - | - | 29 | 49.8 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 28.8 | 1.48 | 4.5 | 4.7 | 0 | 28.2 | 28.1 | 28.9 | 1.49 | 3.4 | 4.1 | 24.8 | 24.6 | 27.4 | 1.52 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:25:00 | 17.14 | 49.76 | 758658.42 | 730724.2 | 5.41 | 4295.256 | 132.84 | -4.138 | 4 | 169 | 26.1 | 56 | 26.2 | 55.8 | 0 | 0 | - | - | 29 | 49.8 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 28.8 | 1.48 | 4.6 | 4.7 | 0 | 28.3 | 28.1 | 28.9 | 1.49 | 3.5 | 4.1 | 24.8 | 24.6 | 27.5 | 1.52 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:30:00 | 17.64 | 50.26 | 758658.92 | 730724.68 | 5.48 | 4280.496 | 147.6 | -3.106 | 4 | 169 | 26.1 | 55.9 | 26.2 | 55.9 | 0 | 0 | - | - | 29 | 49.8 | 0 | 0 | 0 | 0 | 29.3 | 29 | 29 | 1.48 | 4.6 | 4.8 | 0 | 28.4 | 28.2 | 29 | 1.49 | 3.5 | 4.2 | 24.8 | 24.6 | 27.5 | 1.52 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:35:00 | 17.98 | 50.74 | 758659.28 | 730725.2 | 5.55 | 4280.496 | 147.6 | -3.29 | 4 | 169 | 26.1 | 55.9 | 26.3 | 55.8 | 0 | 0 | - | - | 29 | 49.7 | 0 | 0 | 0 | 0 | 29.3 | 29 | 28.9 | 1.48 | 4.7 | 4.9 | 0 | 28.4 | 28.2 | 29 | 1.49 | 3.6 | 4.2 | 24.8 | 24.6 | 27.3 | 1.52 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:40:00 | 18.38 | 51.38 | 758659.7 | 730725.8 | 5.62 | 4295.256 | 132.84 | 0.028 | 4 | 169 | 26.2 | 55.9 | 26.2 | 55.9 | 0 | 0 | - | - | 29 | 49.8 | 0 | 0 | 0 | 0 | 29.2 | 29 | 28.8 | 1.48 | 4.6 | 4.7 | 0 | 28.3 | 28.2 | 29 | 1.49 | 3.6 | 4.2 | 24.8 | 24.7 | 27.4 | 1.52 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:45:00 | 18.8 | 52.06 | 758660.08 | 730726.48 | 5.69 | 4295.256 | 132.84 | -1.895 | 4 | 169 | 26.2 | 55.8 | 26.2 | 56 | 0 | 0 | - | - | 29 | 49.8 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 28.8 | 1.48 | 4.5 | 4.6 | 0 | 28.3 | 28.2 | 29 | 1.49 | 3.5 | 4.1 | 24.8 | 24.7 | 27.6 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:50:00 | 19.26 | 52.58 | 758660.56 | 730727 | 5.76 | 4280.496 | 147.6 | -2.821 | 4 | 169 | 26.2 | 55.8 | 26.2 | 56 | 0 | 0 | - | - | 29.1 | 49.8 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 28.8 | 1.48 | 4.5 | 4.5 | 0 | 28.2 | 28.1 | 29 | 1.49 | 3.5 | 4.1 | 24.8 | 24.7 | 27.8 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 06:55:00 | 19.6 | 53.14 | 758660.9 | 730727.58 | 5.83 | 4295.256 | 132.84 | -0.613 | 4 | 169 | 26.3 | 55.8 | 26.3 | 55.8 | 0 | 0 | - | - | 29.1 | 49.8 | 0 | 0 | 0 | 0 | 29.2 | 29 | 29 | 1.48 | 4.6 | 4.7 | 0 | 28.4 | 28.2 | 29 | 1.49 | 3.5 | 4.2 | 24.9 | 24.7 | 27.8 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:00:00 | 20 | 53.74 | 758661.28 | 730728.16 | 5.9 | 4295.256 | 132.84 | -5.546 | 4 | 169 | 26.3 | 55.7 | 26.4 | 55.7 | 0 | 0 | - | - | 29.1 | 49.7 | 0 | 0 | 0 | 0 | 29.4 | 29.1 | 29.4 | 1.48 | 4.7 | 4.9 | 0 | 28.5 | 28.2 | 29.2 | 1.49 | 3.6 | 4.3 | 24.8 | 24.7 | 28 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:05:00 | 20.36 | 54.22 | 758661.64 | 730728.64 | 5.97 | 4295.256 | 132.84 | -10.176 | 4 | 169 | 26.4 | 55.7 | 26.4 | 55.7 | 0 | 0 | - | - | 29.1 | 49.7 | 0 | 0 | 0 | 0 | 29.5 | 29.2 | 29.4 | 1.48 | 4.7 | 5 | 0 | 28.6 | 28.3 | 29.2 | 1.49 | 3.6 | 4.4 | 24.9 | 24.7 | 28 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:10:00 | 20.66 | 54.7 | 758661.94 | 730729.14 | 6.04 | 4273.116 | 154.98 | -2.175 | 4 | 169 | 26.4 | 55.6 | 26.5 | 55.6 | 0 | 0 | - | - | 29.2 | 49.6 | 0 | 0 | 0 | 0 | 29.5 | 29.2 | 29.4 | 1.48 | 4.7 | 5 | 0 | 28.6 | 28.3 | 29.3 | 1.49 | 3.7 | 4.4 | 24.9 | 24.7 | 28.2 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:15:00 | 21.02 | 55.3 | 758662.3 | 730729.72 | 6.11 | 4273.116 | 154.98 | -3.401 | 4 | 169 | 26.5 | 55.5 | 26.5 | 55.6 | 0 | 0 | - | - | 29.3 | 49.5 | 0 | 0 | 0 | 0 | 29.5 | 29.2 | 29.4 | 1.49 | 4.7 | 4.9 | 0 | 28.6 | 28.3 | 29.4 | 1.49 | 3.7 | 4.4 | 24.9 | 24.7 | 28.4 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:20:00 | 21.44 | 55.9 | 758662.72 | 730730.32 | 6.18 | 4295.256 | 132.84 | -4.282 | 4 | 169 | 26.5 | 55.5 | 26.6 | 55.5 | 0 | 0 | - | - | 29.3 | 49.5 | 0 | 0 | 0 | 0 | 29.5 | 29.3 | 29.4 | 1.49 | 4.8 | 4.9 | 0 | 28.6 | 28.4 | 29.5 | 1.49 | 3.7 | 4.4 | 24.9 | 24.7 | 28.3 | 1.53 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:25:00 | 22.26 | 57.8 | 758663.56 | 730732.22 | 6.25 | 4295.256 | 132.84 | 18.574 | 4 | 169 | 26.6 | 55.3 | 26.7 | 55.4 | 0 | 0 | - | - | 29.4 | 49.4 | 0 | 0 | 0 | 0 | 29.6 | 29.3 | 29.5 | 1.49 | 4.8 | 4.9 | 0 | 28.7 | 28.4 | 29.6 | 1.5 | 3.7 | 4.4 | 24.9 | 24.7 | 28.3 | 1.53 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:30:00 | 23.44 | 58.04 | 758664.74 | 730732.46 | 6.32 | 4273.116 | 154.98 | 10.129 | 4 | 169 | 26.7 | 55.2 | 26.8 | 55.3 | 0 | 0 | - | - | 29.4 | 49.4 | 0 | 0 | 0 | 0 | 29.6 | 29.3 | 29.6 | 1.49 | 4.8 | 4.9 | 0 | 28.7 | 28.5 | 29.6 | 1.5 | 3.7 | 4.5 | 25 | 24.8 | 28.6 | 1.53 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:35:00 | 24.54 | 58.4 | 758665.84 | 730732.82 | 6.39 | 4295.256 | 132.84 | 8.782 | 4 | 169 | 26.8 | 55 | 26.8 | 55.3 | 0 | 0 | - | - | 29.5 | 49.3 | 0 | 0 | 0 | 0 | 29.6 | 29.3 | 29.6 | 1.49 | 4.8 | 4.9 | 0 | 28.8 | 28.5 | 29.7 | 1.5 | 3.7 | 4.5 | 25 | 24.7 | 28.7 | 1.53 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:40:00 | 25.6 | 58.84 | 758666.9 | 730733.26 | 6.47 | 4273.116 | 154.98 | 6.732 | 4 | 169 | 26.9 | 54.9 | 26.9 | 55.2 | 0 | 0 | - | - | 29.6 | 49.3 | 0 | 0 | 0 | 0 | 29.7 | 29.4 | 29.7 | 1.49 | 4.8 | 5 | 0 | 28.8 | 28.6 | 29.8 | 1.5 | 3.8 | 4.5 | 25 | 24.8 | 29.1 | 1.53 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:45:00 | 26.76 | 59.22 | 758668.04 | 730733.64 | 6.53 | 4295.256 | 132.84 | -18.866 | 4 | 169 | 27.1 | 54.8 | 27 | 55.1 | 0 | 0 | - | - | 29.6 | 49.2 | 0 | 0 | 0 | 0 | 29.8 | 29.5 | 29.9 | 1.49 | 4.9 | 5.1 | 0 | 29 | 28.6 | 30 | 1.5 | 3.8 | 4.6 | 25 | 24.8 | 29.2 | 1.53 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:50:00 | 27.9 | 59.58 | 758669.2 | 730734.02 | 6.6 | 4287.876 | 140.22 | 10.521 | 4 | 169 | 27.2 | 54.6 | 27.1 | 54.9 | 0 | 0 | - | - | 29.7 | 49.1 | 0 | 0 | 0 | 0 | 29.9 | 29.6 | 30 | 1.49 | 5 | 5.2 | 0 | 29.1 | 28.7 | 30.2 | 1.5 | 3.9 | 4.7 | 25 | 24.8 | 29.3 | 1.53 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 07:55:00 | 28.9 | 60.1 | 758670.22 | 730734.52 | 6.68 | 4280.496 | 147.6 | 9.008 | 4 | 169 | 27.3 | 54.4 | 27.2 | 54.8 | 0 | 0 | - | - | 29.8 | 49 | 0 | 0 | 0 | 0 | 30.1 | 29.7 | 30.1 | 1.49 | 5 | 5.3 | 0 | 29.2 | 28.8 | 30.2 | 1.5 | 4 | 4.8 | 25 | 24.8 | 29.5 | 1.53 | 1.53 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:00:00 | 30.02 | 60.94 | 758671.3 | 730735.38 | 6.75 | 4295.256 | 132.84 | 9.076 | 4 | 169 | 27.4 | 54.2 | 27.3 | 54.6 | 0 | 0 | - | - | 29.9 | 48.9 | 0 | 0 | 0 | 0 | 30.1 | 29.7 | 30.2 | 1.49 | 5.1 | 5.4 | 0 | 29.3 | 28.9 | 30.4 | 1.5 | 4 | 4.9 | 25 | 24.8 | 29.7 | 1.53 | 1.53 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:05:00 | 31.1 | 61.42 | 758672.38 | 730735.84 | 6.82 | 4295.256 | 132.84 | -7.85 | 4 | 169 | 27.6 | 54 | 27.4 | 54.5 | 0 | 0 | - | - | 30 | 48.9 | 0 | 0 | 0 | 0 | 30.2 | 29.8 | 30.3 | 1.49 | 5.2 | 5.5 | 0 | 29.4 | 29 | 30.5 | 1.5 | 4.1 | 4.9 | 25 | 24.8 | 29.8 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:10:00 | 32.26 | 61.88 | 758673.56 | 730736.34 | 6.89 | 4295.256 | 132.84 | 2.536 | 4 | 169 | 27.7 | 53.8 | 27.5 | 54.3 | 0 | 0 | - | - | 30.1 | 48.7 | 0 | 0 | 0 | 0 | 30.5 | 29.9 | 30.6 | 1.49 | 5.3 | 5.7 | 0 | 29.5 | 29.1 | 30.7 | 1.5 | 4.2 | 5.1 | 25 | 24.9 | 29.8 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:15:00 | 33.34 | 62.36 | 758674.62 | 730736.8 | 6.96 | 4295.256 | 132.84 | 8.384 | 4 | 169 | 27.9 | 53.6 | 27.7 | 54.1 | 0 | 0 | - | - | 30.2 | 48.6 | 0 | 0 | 0 | 0 | 30.6 | 30 | 30.6 | 1.49 | 5.3 | 5.8 | 0 | 29.7 | 29.2 | 30.7 | 1.5 | 4.3 | 5.2 | 25 | 24.8 | 29.9 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:20:00 | 34.14 | 62.9 | 758675.44 | 730737.34 | 7.03 | 4295.256 | 132.84 | 2.352 | 4 | 169 | 28 | 53.3 | 27.8 | 54 | 0 | 0 | - | - | 30.3 | 48.5 | 0 | 0 | 0 | 0 | 30.7 | 30.1 | 30.8 | 1.49 | 5.4 | 5.9 | 0 | 29.8 | 29.3 | 30.9 | 1.5 | 4.4 | 5.3 | 25.1 | 24.8 | 30.1 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:25:00 | 34.9 | 63.48 | 758676.18 | 730737.9 | 7.1 | 4280.496 | 147.6 | 1.848 | 4 | 169 | 28.2 | 53.1 | 27.9 | 53.8 | 0 | 0 | - | - | 30.5 | 48.4 | 0 | 0 | 0 | 0 | 31 | 30.3 | 31 | 1.5 | 5.6 | 6.1 | 0 | 30 | 29.5 | 31.2 | 1.5 | 4.6 | 5.5 | 25.1 | 24.9 | 30.3 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:30:00 | 35.62 | 64.08 | 758676.9 | 730738.5 | 7.17 | 4295.256 | 132.84 | 5.14 | 4 | 169 | 28.4 | 52.8 | 28 | 53.6 | 0 | 0 | - | - | 30.6 | 48.2 | 0 | 0 | 0 | 0 | 31.1 | 30.3 | 31.2 | 1.5 | 5.6 | 6.3 | 0 | 30.2 | 29.6 | 31.3 | 1.51 | 4.7 | 5.6 | 25.1 | 24.9 | 30.3 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:35:00 | 36.2 | 64.6 | 758677.5 | 730739.02 | 7.24 | 4295.256 | 132.84 | 1.519 | 4 | 169 | 28.5 | 52.7 | 28.1 | 53.5 | 0 | 0 | - | - | 30.7 | 48.1 | 0 | 0 | 0 | 0 | 31.1 | 30.3 | 31.2 | 1.5 | 5.6 | 6.3 | 0 | 30.2 | 29.6 | 31.3 | 1.51 | 4.7 | 5.6 | 25.1 | 24.9 | 30.4 | 1.54 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:40:00 | 36.58 | 65.24 | 758677.86 | 730739.68 | 7.31 | 4295.256 | 132.84 | -3.131 | 4 | 169 | 28.7 | 52.5 | 28.3 | 53.3 | 0 | 0 | - | - | 30.9 | 48 | 0 | 0 | 0 | 0 | 31.2 | 30.4 | 31.3 | 1.5 | 5.7 | 6.3 | 0 | 30.2 | 29.7 | 31.5 | 1.51 | 4.7 | 5.7 | 25.1 | 24.9 | 30.5 | 1.54 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:45:00 | 36.7 | 66.02 | 758677.98 | 730740.44 | 7.38 | 4295.256 | 132.84 | -7.872 | 4 | 169 | 28.8 | 52.4 | 28.4 | 53.2 | 0 | 0 | - | - | 31 | 47.9 | 0 | 0 | 0 | 0 | 31.3 | 30.4 | 31.4 | 1.5 | 5.7 | 6.4 | 0 | 30.3 | 29.8 | 31.6 | 1.51 | 4.8 | 5.8 | 25.1 | 24.9 | 30.7 | 1.54 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:50:00 | 36.74 | 66.74 | 758678.02 | 730741.16 | 7.45 | 4295.256 | 132.84 | -28.056 | 4 | 169 | 28.9 | 52.1 | 28.5 | 53.1 | 0 | 0 | - | - | 31.1 | 47.7 | 0 | 0 | 0 | 0 | 31.3 | 30.5 | 31.5 | 1.5 | 5.7 | 6.4 | 0 | 30.5 | 29.9 | 31.7 | 1.51 | 4.9 | 5.9 | 25.1 | 24.9 | 30.9 | 1.54 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 08:55:00 | 36.78 | 67.58 | 758678.06 | 730742.02 | 7.52 | 4295.256 | 132.84 | -16.648 | 4 | 169 | 29 | 52 | 28.6 | 52.9 | 0 | 0 | - | - | 31.3 | 47.6 | 0 | 0 | 0 | 0 | 31.5 | 30.6 | 31.6 | 1.5 | 5.8 | 6.6 | 0 | 30.6 | 30 | 31.9 | 1.51 | 5 | 5.9 | 25.2 | 25 | 31 | 1.54 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:00:00 | 37 | 68.26 | 758678.28 | 730742.7 | 7.58 | 4273.116 | 154.98 | -3.263 | 4 | 169 | 29.1 | 51.9 | 28.6 | 52.9 | 0 | 0 | - | - | 31.4 | 47.5 | 0 | 0 | 0 | 0 | 31.6 | 30.7 | 31.8 | 1.5 | 5.8 | 6.6 | 0 | 30.6 | 30.1 | 32.1 | 1.51 | 5.1 | 6 | 25.2 | 25 | 31.2 | 1.54 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:05:00 | 37.34 | 68.88 | 758678.64 | 730743.3 | 7.65 | 4273.116 | 154.98 | -6.898 | 4 | 169 | 29.3 | 51.8 | 28.7 | 52.8 | 0 | 0 | - | - | 31.5 | 47.3 | 0 | 0 | 0 | 0 | 31.7 | 30.8 | 31.9 | 1.5 | 5.9 | 6.7 | 0 | 30.8 | 30.2 | 32.2 | 1.51 | 5.1 | 6.1 | 25.2 | 25 | 31.3 | 1.54 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:10:00 | 37.74 | 69.52 | 758679.02 | 730743.94 | 7.72 | 4295.256 | 132.84 | -3.434 | 4 | 169 | 29.4 | 51.6 | 28.8 | 52.7 | 0 | 0 | - | - | 31.7 | 47.3 | 0 | 0 | 0 | 0 | 31.8 | 30.8 | 32 | 1.5 | 6 | 6.9 | 0 | 30.9 | 30.3 | 32.4 | 1.51 | 5.2 | 6.2 | 25.2 | 25 | 31.3 | 1.54 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:15:00 | 38.26 | 70 | 758679.54 | 730744.46 | 7.79 | 4273.116 | 154.98 | 0.1 | 4 | 169 | 29.4 | 51.6 | 29.2 | 52.1 | 0 | 0 | - | - | 31.8 | 47.1 | 0 | 0 | 0 | 0 | 31.9 | 30.9 | 32.1 | 1.5 | 6 | 6.9 | 0 | 30.9 | 30.4 | 32.5 | 1.51 | 5.3 | 6.2 | 25.3 | 25 | 31.7 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:20:00 | 38.94 | 70.58 | 758680.22 | 730745 | 7.87 | 4295.256 | 132.84 | 1.403 | 4 | 169 | 29.5 | 51.6 | 29.5 | 51.7 | 0 | 0 | - | - | 32 | 47 | 0 | 0 | 0 | 0 | 32 | 31 | 32.2 | 1.5 | 6.1 | 7 | 0 | 31.1 | 30.5 | 32.6 | 1.51 | 5.4 | 6.4 | 25.3 | 25.1 | 31.6 | 1.54 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:25:00 | 39.66 | 70.94 | 758680.96 | 730745.36 | 7.94 | 4273.116 | 154.98 | 1.178 | 4 | 169 | 29.6 | 51.3 | 29.3 | 52 | 0 | 0 | - | - | 32.1 | 46.9 | 0 | 0 | 0 | 0 | 32.2 | 31.1 | 32.4 | 1.5 | 6.3 | 7.2 | 0 | 31.2 | 30.6 | 32.7 | 1.51 | 5.5 | 6.5 | 25.2 | 25.1 | 31.7 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:30:00 | 40.4 | 71.28 | 758681.7 | 730745.7 | 8.01 | 4273.116 | 154.98 | 11.93 | 4 | 169 | 29.8 | 51.2 | 29.2 | 52.1 | 0 | 0 | - | - | 32.2 | 46.7 | 0 | 0 | 0 | 0 | 32.3 | 31.1 | 32.5 | 1.5 | 6.3 | 7.3 | 0 | 31.3 | 30.7 | 32.8 | 1.51 | 5.5 | 6.6 | 25.3 | 25.1 | 31.9 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:35:00 | 41.16 | 71.56 | 758682.44 | 730745.98 | 8.08 | 4273.116 | 154.98 | 1.573 | 4 | 169 | 29.9 | 51 | 29.3 | 52.1 | 0 | 0 | - | - | 32.3 | 46.6 | 0 | 0 | 0 | 0 | 32.4 | 31.2 | 32.6 | 1.5 | 6.3 | 7.4 | 0 | 31.4 | 30.7 | 32.9 | 1.51 | 5.6 | 6.7 | 25.3 | 25.1 | 31.9 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:40:00 | 41.86 | 72 | 758683.16 | 730746.42 | 8.15 | 4273.116 | 154.98 | 2.73 | 4 | 169 | 30 | 50.9 | 29.4 | 52 | 0 | 0 | - | - | 32.5 | 46.5 | 0 | 0 | 0 | 0 | 32.5 | 31.2 | 32.7 | 1.51 | 6.3 | 7.4 | 0 | 31.6 | 30.8 | 33 | 1.51 | 5.6 | 6.8 | 25.3 | 25.1 | 31.8 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:45:00 | 42.52 | 72.46 | 758683.8 | 730746.88 | 8.23 | 4295.256 | 132.84 | 0.697 | 4 | 169 | 30.1 | 50.8 | 29.5 | 52 | 0 | 0 | - | - | 32.6 | 46.4 | 0 | 0 | 0 | 0 | 32.6 | 31.3 | 32.7 | 1.51 | 6.3 | 7.5 | 0 | 31.6 | 30.8 | 33.2 | 1.52 | 5.7 | 6.8 | 25.3 | 25.1 | 32.3 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:50:00 | 43.22 | 72.94 | 758684.52 | 730747.38 | 8.3 | 4295.256 | 132.84 | -1.39 | 4 | 169 | 30.2 | 50.7 | 29.5 | 51.9 | 0 | 0 | - | - | 32.8 | 46.3 | 0 | 0 | 0 | 0 | 32.7 | 31.4 | 32.9 | 1.5 | 6.5 | 7.6 | 0 | 31.7 | 30.9 | 33.3 | 1.51 | 5.8 | 7 | 25.3 | 25.1 | 32.4 | 1.55 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 09:55:00 | 44.16 | 73.38 | 758685.44 | 730747.8 | 8.37 | 4295.256 | 132.84 | 5.472 | 4 | 169 | 30.3 | 50.6 | 29.6 | 51.9 | 0 | 0 | - | - | 32.9 | 46.2 | 0 | 0 | 0 | 0 | 32.7 | 31.5 | 33 | 1.51 | 6.5 | 7.7 | 0 | 31.7 | 30.9 | 33.4 | 1.51 | 5.8 | 7 | 25.3 | 25.2 | 32.4 | 1.55 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:00:00 | 45.16 | 73.72 | 758686.52 | 730748.16 | 8.44 | 4295.256 | 132.84 | 7.597 | 4 | 169 | 30.4 | 50.5 | 29.6 | 51.8 | 0 | 0 | - | - | 33 | 46.1 | 0 | 0 | 0 | 0 | 32.8 | 31.6 | 33.1 | 1.51 | 6.5 | 7.7 | 0 | 31.8 | 31 | 33.5 | 1.52 | 5.8 | 7.1 | 25.3 | 25.2 | 32.3 | 1.55 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:05:00 | 46.24 | 74.14 | 758687.52 | 730748.56 | 8.51 | 4273.116 | 154.98 | 6.074 | 4 | 169 | 30.4 | 50.4 | 29.7 | 51.7 | 0 | 0 | - | - | 33.1 | 46 | 0 | 0 | 0 | 0 | 32.9 | 31.6 | 33.1 | 1.51 | 6.6 | 7.7 | 0 | 31.9 | 31.1 | 33.6 | 1.52 | 5.8 | 7.1 | 25.4 | 25.2 | 32.3 | 1.55 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:10:00 | 47.28 | 74.5 | 758688.64 | 730748.92 | 8.59 | 4295.256 | 132.84 | 8.844 | 4 | 169 | 30.5 | 50.4 | 29.8 | 51.6 | 0 | 0 | - | - | 33.2 | 45.9 | 0 | 0 | 0 | 0 | 32.9 | 31.7 | 33.1 | 1.51 | 6.6 | 7.7 | 0 | 31.9 | 31.1 | 33.7 | 1.52 | 5.9 | 7.1 | 25.4 | 25.2 | 32.4 | 1.55 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:15:00 | 48.06 | 75.06 | 758689.34 | 730749.48 | 8.66 | 4295.256 | 132.84 | -2.481 | 4 | 169 | 30.5 | 50.4 | 29.9 | 51.5 | 0 | 0 | - | - | 33.3 | 45.8 | 0 | 0 | 0 | 0 | 33 | 31.7 | 33.2 | 1.51 | 6.7 | 7.8 | 0 | 32.1 | 31.2 | 33.7 | 1.52 | 5.9 | 7.2 | 25.4 | 25.2 | 32.5 | 1.55 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:20:00 | 48.78 | 75.54 | 758690.08 | 730749.96 | 8.74 | 4273.116 | 154.98 | -20.109 | 4 | 169 | 30.6 | 50.3 | 29.9 | 51.4 | 0 | 0 | - | - | 33.4 | 45.7 | 0 | 0 | 0 | 0 | 33 | 31.7 | 33.3 | 1.51 | 6.7 | 7.8 | 0 | 32.1 | 31.2 | 33.8 | 1.52 | 5.9 | 7.3 | 25.4 | 25.2 | 32.5 | 1.55 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:25:00 | 49.48 | 76.18 | 758690.78 | 730750.6 | 8.81 | 4295.256 | 132.84 | 1.21 | 4 | 169 | 30.7 | 50.2 | 30 | 51.3 | 0 | 0 | - | - | 33.5 | 45.6 | 0 | 0 | 0 | 0 | 33.1 | 31.8 | 33.4 | 1.51 | 6.7 | 7.9 | 0 | 32.2 | 31.3 | 33.9 | 1.52 | 6 | 7.3 | 25.4 | 25.3 | 32.6 | 1.55 | 1.55 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:30:00 | 50 | 76.88 | 758691.28 | 730751.3 | 8.89 | 4295.256 | 132.84 | -5.191 | 4 | 169 | 30.8 | 50.1 | 30.1 | 51.3 | 0 | 0 | - | - | 33.6 | 45.5 | 0 | 0 | 0 | 0 | 33.1 | 31.8 | 33.4 | 1.51 | 6.7 | 7.9 | 0 | 32.3 | 31.3 | 34 | 1.52 | 6 | 7.4 | 25.5 | 25.3 | 33.1 | 1.55 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:35:00 | 50.44 | 77.62 | 758691.72 | 730752.08 | 8.97 | 4295.256 | 132.84 | -6.014 | 4 | 169 | 30.9 | 50.1 | 30.2 | 51.2 | 0 | 0 | - | - | 33.7 | 45.4 | 0 | 0 | 0 | 0 | 33.3 | 31.9 | 33.6 | 1.51 | 6.8 | 8 | 0 | 32.4 | 31.4 | 34.1 | 1.52 | 6.1 | 7.5 | 25.5 | 25.3 | 33.1 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:40:00 | 50.8 | 78.22 | 758692.1 | 730752.64 | 9.04 | 4280.496 | 147.6 | -3.376 | 4 | 169 | 30.9 | 50 | 30.3 | 51.2 | 0 | 0 | - | - | 33.9 | 45.3 | 0 | 0 | 0 | 0 | 33.4 | 32 | 33.6 | 1.51 | 6.8 | 8 | 0 | 32.5 | 31.5 | 34.3 | 1.52 | 6.1 | 7.6 | 25.5 | 25.3 | 32.9 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:45:00 | 51.26 | 79.02 | 758692.56 | 730753.44 | 9.12 | 4295.256 | 132.84 | -2.702 | 4 | 169 | 31 | 49.9 | 30.3 | 51.1 | 0 | 0 | - | - | 33.9 | 45.2 | 0 | 0 | 0 | 0 | 33.5 | 32.1 | 33.9 | 1.51 | 7 | 8.4 | 0 | 32.6 | 31.6 | 34.3 | 1.52 | 6.2 | 7.8 | 25.5 | 25.3 | 32.9 | 1.55 | 1.54 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:50:00 | 51.68 | 79.74 | 758693 | 730754.16 | 9.19 | 4295.256 | 132.84 | -1.184 | 4 | 169 | 31 | 49.8 | 30.4 | 51 | 0 | 0 | - | - | 34 | 45.1 | 0 | 0 | 0 | 0 | 33.8 | 32.2 | 33.9 | 1.51 | 7.1 | 8.6 | 0 | 32.7 | 31.6 | 34.2 | 1.52 | 6.3 | 7.9 | 25.6 | 25.3 | 33.2 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 10:55:00 | 52.12 | 80.44 | 758693.4 | 730754.88 | 9.27 | 4295.256 | 132.84 | -1.271 | 4 | 169 | 31.2 | 49.8 | 30.6 | 50.8 | 0 | 0 | - | - | 34.2 | 45 | 0 | 0 | 0 | 0 | 33.9 | 32.3 | 34 | 1.51 | 7.2 | 8.7 | 0 | 32.9 | 31.7 | 34.3 | 1.52 | 6.3 | 8 | 25.6 | 25.4 | 33.4 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:00:00 | 63.9 | 80.72 | 758705.98 | 730755.14 | 9.35 | 4287.876 | 140.22 | 396.119 | 4 | 169 | 31.3 | 49.7 | 30.7 | 50.7 | 0 | 0 | - | - | 34.3 | 45 | 0 | 0 | 0 | 0 | 34.1 | 32.5 | 34.3 | 1.51 | 7.4 | 8.8 | 0 | 33 | 31.8 | 34.3 | 1.52 | 6.5 | 8.1 | 25.6 | 25.4 | 33.5 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:05:00 | 119.3 | 80.72 | 758761.08 | 730755.14 | 9.44 | 4228.836 | 199.26 | 1008.679 | 5 | 169 | 31.4 | 49.6 | 30.7 | 50.8 | 0 | 0 | - | - | 34.4 | 44.9 | 0 | 0 | 0 | 0 | 34.1 | 32.4 | 34.3 | 1.51 | 7.3 | 8.9 | 0 | 33.1 | 31.8 | 34.4 | 1.52 | 6.5 | 8.2 | 25.6 | 25.4 | 34 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:10:00 | 209.62 | 80.72 | 758852.82 | 730755.14 | 9.54 | 4132.896 | 295.206 | 1208.9 | 8 | 169 | 31.5 | 49.4 | 30.8 | 50.7 | 0 | 0 | - | - | 34.5 | 44.7 | 0 | 0 | 0 | 0 | 34.3 | 32.5 | 34.4 | 1.51 | 7.4 | 9 | 0 | 33.2 | 31.9 | 34.6 | 1.52 | 6.5 | 8.3 | 25.5 | 25.2 | 34.1 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:15:00 | 311.5 | 80.72 | 758954.06 | 730755.14 | 9.64 | 4044.33 | 383.766 | 1207.246 | 10 | 169 | 31.7 | 49.3 | 30.9 | 50.5 | 0 | 0 | - | - | 34.7 | 44.6 | 0 | 0 | 0 | 0 | 34.5 | 32.8 | 34.7 | 1.51 | 7.7 | 9.2 | 0 | 33.5 | 32.1 | 34.8 | 1.52 | 6.8 | 8.6 | 25.5 | 25.3 | 33.6 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:20:00 | 412.56 | 80.72 | 759056.3 | 730755.14 | 9.75 | 3941.01 | 487.086 | 1210.644 | 12 | 169 | 32.1 | 48.9 | 31.1 | 50.3 | 0 | 0 | - | - | 34.8 | 44.4 | 0 | 0 | 0 | 0 | 34.5 | 32.8 | 34.7 | 1.52 | 7.6 | 9.2 | 0 | 33.5 | 32.2 | 35 | 1.52 | 6.9 | 8.6 | 25.6 | 25.4 | 33.4 | 1.56 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:25:00 | 513.7 | 80.72 | 759157.54 | 730755.14 | 9.87 | 3837.688 | 590.412 | 1219.001 | 15 | 169 | 32.4 | 48.6 | 31.3 | 50.2 | 0 | 0 | - | - | 35 | 44.3 | 0 | 0 | 0 | 0 | 34.4 | 32.7 | 34.7 | 1.52 | 7.5 | 9.1 | 0 | 33.6 | 32.2 | 35.1 | 1.53 | 6.8 | 8.5 | 25.8 | 25.6 | 33.1 | 1.56 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:30:00 | 614.9 | 80.72 | 759258.72 | 730755.14 | 9.99 | 3741.744 | 686.352 | 1215.348 | 17 | 169 | 32.3 | 48.7 | 31.3 | 50.2 | 0 | 0 | - | - | 35.1 | 44.2 | 0 | 0 | 0 | 0 | 34.5 | 32.7 | 34.7 | 1.52 | 7.3 | 9.1 | 0 | 33.6 | 32.2 | 35.2 | 1.53 | 6.7 | 8.5 | 25.9 | 25.8 | 33.4 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:35:00 | 740.6 | 80.72 | 759386.28 | 730755.14 | 10.11 | 3601.52 | 826.578 | 2023.08 | 20 | 169 | 32.2 | 49 | 31.4 | 50.3 | 0 | 0 | - | - | 35.3 | 44.1 | 0 | 0 | 0 | 0 | 34.5 | 32.7 | 34.8 | 1.52 | 7.2 | 9 | 0 | 33.6 | 32.2 | 35.2 | 1.53 | 6.5 | 8.5 | 26.1 | 25.9 | 33.8 | 1.57 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:40:00 | 910.06 | 80.72 | 759555.62 | 730755.14 | 10.26 | 3439.158 | 988.938 | 2025.641 | 24 | 169 | 32.2 | 49 | 31.5 | 50.2 | 0 | 0 | - | - | 35.4 | 44.1 | 0 | 0 | 0 | 0 | 34.6 | 32.7 | 34.9 | 1.53 | 7.1 | 9.1 | 0 | 33.7 | 32.2 | 35.4 | 1.54 | 6.4 | 8.5 | 26.4 | 26.2 | 34.3 | 1.57 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:45:00 | 1080.74 | 80.72 | 759723.04 | 730755.14 | 10.61 | 3254.652 | 1173.444 | 2018.046 | 28 | 169 | 32.4 | 48.9 | 31.8 | 50 | 0 | 0 | - | - | 35.6 | 44 | 0 | 0 | 0 | 0 | 34.8 | 32.9 | 35.2 | 1.53 | 7.1 | 9.1 | 0 | 33.9 | 32.3 | 35.6 | 1.54 | 6.3 | 8.6 | 23.8 | 25.9 | 33.5 | 2.58 | 1.08 | 2.7 | 1.11 | 227 | 188 | 2592 | 2592
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:50:00 | 1244.36 | 80.72 | 759889.9 | 730755.14 | 11.42 | 3084.91 | 1343.19 | 2002.341 | 32 | 169 | 32.8 | 48.6 | 32 | 49.8 | 0 | 0 | - | - | 35.7 | 43.9 | 230 | 187 | 59.2 | 59.2 | 64 | 26.2 | 43.3 | 2.55 | 12.3 | 18.6 | 59.3 | 65 | 25.7 | 45.4 | 2.71 | 11.8 | 17.6 | 21.8 | 23.7 | 35.4 | 2.67 | 1.07 | 2.78 | 1.07 | 241 | 193 | 2607 | 2607
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 11:55:00 | 1415.32 | 80.72 | 760058.74 | 730755.14 | 12.21 | 2929.926 | 1498.171 | 2012.797 | 36 | 169 | 33.1 | 48.2 | 32.2 | 49.5 | 0 | 0 | - | - | 36 | 43.7 | 241 | 193 | 62.3 | 62.3 | 72 | 23.8 | 44.6 | 2.57 | 11.1 | 26.1 | 62.2 | 74.9 | 23.7 | 46.8 | 2.74 | 11 | 27.2 | 21.6 | 23.2 | 35.9 | 2.69 | 1.09 | 2.78 | 1.08 | 241 | 193 | 2334 | 2334
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:00:00 | 1583.4 | 80.72 | 760227.8 | 730755.14 | 12.91 | 2745.42 | 1682.676 | 2015.066 | 40 | 169 | 33.3 | 47.9 | 32.4 | 49.3 | 0 | 0 | - | - | 36.2 | 43.5 | 241 | 193 | 62 | 62 | 72 | 23.6 | 44.7 | 2.53 | 10 | 26.7 | 61.8 | 75.1 | 23.3 | 46.9 | 2.72 | 10.1 | 27.5 | 21.8 | 23.3 | 35.8 | 2.61 | 1.1 | 2.74 | 1.09 | 241 | 193 | 2277 | 2277
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:05:00 | 1750.4 | 80.72 | 760394.98 | 730755.14 | 13.61 | 2583.06 | 1845.042 | 2013.683 | 44 | 170 | 33.5 | 47.8 | 32.7 | 49 | 0 | 0 | - | - | 36.5 | 43.3 | 241 | 193 | 59.9 | 60.2 | 70.5 | 23.7 | 44 | 2.53 | 10.2 | 25.2 | 60 | 74.2 | 23.5 | 46.3 | 2.7 | 10.2 | 27.1 | 22 | 23.7 | 36.7 | 2.61 | 1.1 | 2.74 | 1.1 | 241 | 193 | 2277 | 2277
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:10:00 | 1921.88 | 80.72 | 760566.4 | 730755.14 | 14.31 | 2420.694 | 2007.402 | 1746.266 | 48 | 170 | 33.5 | 47.9 | 32.9 | 48.9 | 0 | 0 | - | - | 36.7 | 43.2 | 241 | 193 | 59.6 | 59.7 | 70.4 | 24 | 44 | 2.54 | 10.2 | 25.1 | 60 | 74.1 | 23.8 | 46.3 | 2.7 | 10.2 | 27 | 22.3 | 24 | 35.9 | 2.62 | 1.11 | 2.75 | 1.1 | 241 | 193 | 2277 | 2277
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:15:00 | 2067.84 | 80.72 | 760710 | 730755.14 | 15.02 | 2265.708 | 2162.388 | 1559.194 | 51 | 170 | 33.6 | 47.9 | 33.2 | 48.6 | 0 | 0 | - | - | 37 | 43 | 241 | 193 | 60 | 60.1 | 70.1 | 24.3 | 43.8 | 2.51 | 10.5 | 25.1 | 59.6 | 73.8 | 24.1 | 46.3 | 2.7 | 10.3 | 26.7 | 22.7 | 24.4 | 36.7 | 2.71 | 1.12 | 2.81 | 1.11 | 241 | 193 | 2277 | 2277
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:20:00 | 2197.64 | 80.72 | 760842.16 | 730755.14 | 15.75 | 2118.108 | 2309.989 | 1559.63 | 54 | 170 | 33.8 | 47.8 | 33.5 | 48.5 | 0 | 0 | - | - | 37.2 | 42.8 | 241 | 193 | 62.4 | 62.1 | 71.3 | 24.7 | 45.1 | 2.59 | 10.4 | 25.1 | 62 | 75 | 24.6 | 47.2 | 2.77 | 10.5 | 26.9 | 23.1 | 24.7 | 35.9 | 2.67 | 1.13 | 2.8 | 1.13 | 241 | 193 | 2277 | 2277
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:25:00 | 2327.44 | 80.72 | 760971.12 | 730755.14 | 16.46 | 1985.262 | 2442.834 | 1580.325 | 57 | 170 | 34 | 47.7 | 33.7 | 48.3 | 0 | 0 | - | - | 37.5 | 42.7 | 241 | 193 | 60.8 | 60.7 | 71.1 | 25.1 | 44.6 | 2.51 | 10.5 | 26.2 | 61.1 | 75.1 | 24.9 | 47.2 | 2.73 | 10.4 | 27.4 | 23.4 | 25 | 35.4 | 2.67 | 1.13 | 2.81 | 1.13 | 241 | 193 | 2281 | 2281
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:30:00 | 2458.84 | 80.72 | 761101.82 | 730755.14 | 17.18 | 1852.422 | 2575.68 | 1563.655 | 60 | 170 | 34.2 | 47.7 | 34 | 48.1 | 0 | 0 | - | - | 37.7 | 42.5 | 241 | 193 | 62.1 | 62.1 | 70.7 | 25.3 | 44.6 | 2.63 | 10.7 | 24 | 62.3 | 74.8 | 25.2 | 47.2 | 2.78 | 10.8 | 26.4 | 23.7 | 25.4 | 36.2 | 2.72 | 1.14 | 2.83 | 1.14 | 241 | 193 | 2292 | 2292
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:35:00 | 2575.5 | 80.72 | 761219.2 | 730755.14 | 17.91 | 1749.096 | 2679 | 1157.835 | 63 | 170 | 34.5 | 47.5 | 34.3 | 47.8 | 0 | 0 | - | - | 38 | 42.3 | 241 | 193 | 63.2 | 62.9 | 72.1 | 25.7 | 45.6 | 2.64 | 10.8 | 25.1 | 62.6 | 75.7 | 25.5 | 47.7 | 2.8 | 10.8 | 27.1 | 24 | 25.7 | 36.6 | 2.67 | 1.14 | 2.84 | 1.14 | 241 | 193 | 2313 | 2313
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:40:00 | 2673.74 | 80.72 | 761316.26 | 730755.14 | 18.68 | 1631.016 | 2797.081 | 1163.662 | 65 | 170 | 34.8 | 47.3 | 34.6 | 47.6 | 0 | 0 | - | - | 38.3 | 42 | 241 | 193 | 61.6 | 61.5 | 71.5 | 26 | 44.4 | 2.54 | 10.9 | 26.2 | 61.9 | 75.9 | 25.9 | 47.6 | 2.77 | 10.6 | 27.5 | 24.2 | 25.9 | 36.9 | 2.73 | 1.14 | 2.88 | 1.15 | 241 | 193 | 2389 | 2389
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:45:00 | 2770.18 | 80.72 | 761413.26 | 730755.14 | 19.45 | 1535.074 | 2893.026 | 1160.924 | 67 | 170 | 35 | 47.2 | 34.9 | 47.4 | 0 | 0 | - | - | 38.6 | 41.9 | 241 | 193 | 64.3 | 64.2 | 72.8 | 26.1 | 45.4 | 2.61 | 11.2 | 26.4 | 64.1 | 76.9 | 26 | 48.2 | 2.83 | 11.1 | 27.9 | 24.2 | 25.9 | 35.7 | 2.69 | 1.15 | 2.84 | 1.15 | 241 | 193 | 2415 | 2415
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:50:00 | 2864.36 | 80.72 | 761507.16 | 730755.14 | 20.23 | 1439.13 | 2988.966 | 956.375 | 69 | 170 | 35.3 | 46.9 | 35.1 | 47.3 | 0 | 0 | - | - | 38.8 | 41.7 | 241 | 193 | 63.4 | 63.3 | 72.4 | 26.2 | 45.2 | 2.6 | 11.2 | 26.2 | 63.6 | 76.4 | 26.1 | 47.9 | 2.81 | 10.9 | 27.5 | 24.3 | 26 | 35 | 2.69 | 1.15 | 2.85 | 1.15 | 241 | 193 | 2415 | 2415
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 12:55:00 | 2921.8 | 80.72 | 761563.34 | 730755.14 | 21.01 | 1380.09 | 3048.007 | 182.485 | 70 | 170 | 35.6 | 46.7 | 35.4 | 47.1 | 0 | 0 | - | - | 39 | 41.7 | 241 | 193 | 62.7 | 63.1 | 71.7 | 26.3 | 44.7 | 2.58 | 11.2 | 25.7 | 63.1 | 75.9 | 26.1 | 47.8 | 2.8 | 10.8 | 27.3 | 24.4 | 26.1 | 35.6 | 2.67 | 1.15 | 2.86 | 1.16 | 241 | 193 | 2442 | 2451
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:00:00 | 2934.08 | 80.96 | 761575.36 | 730755.42 | 21.8 | 1372.71 | 3055.387 | -12.997 | 71 | 170 | 35.6 | 46.7 | 35.5 | 47.1 | 0 | 0 | - | - | 39.2 | 41.6 | 241 | 193 | 63.9 | 63.8 | 72.4 | 26.4 | 45.1 | 2.6 | 11.4 | 26.1 | 63.9 | 76.8 | 26.2 | 48.1 | 2.82 | 11.1 | 27.8 | 24.2 | 26.1 | 35.1 | 2.67 | 1.15 | 2.87 | 1.16 | 242 | 193 | 2550 | 2550
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:05:00 | 2937.02 | 82.3 | 761578.68 | 730756.72 | 22.61 | 1365.33 | 3062.767 | 177.071 | 71 | 170 | 35.9 | 46.5 | 35.7 | 46.8 | 0 | 0 | - | - | 39.3 | 41.6 | 242 | 193 | 64.4 | 64.3 | 72.6 | 26.2 | 45 | 2.62 | 11.3 | 26 | 64.1 | 76.8 | 26.2 | 48.1 | 2.84 | 11 | 27.6 | 24.1 | 25.8 | 34.5 | 2.66 | 1.14 | 2.85 | 1.15 | 242 | 193 | 2550 | 2550
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:10:00 | 2973.28 | 82.3 | 761614.56 | 730756.72 | 23.42 | 1321.05 | 3107.051 | 574.031 | 72 | 170 | 35.9 | 46.4 | 35.6 | 46.9 | 0 | 0 | - | - | 39.3 | 41.6 | 242 | 193 | 63.3 | 62.7 | 72.4 | 26.1 | 44.8 | 2.59 | 11.3 | 26.3 | 63 | 76.4 | 25.9 | 47.7 | 2.79 | 11 | 27.9 | 23.8 | 25.7 | 35.1 | 2.68 | 1.14 | 2.87 | 1.15 | 242 | 193 | 2553 | 2553
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:15:00 | 3026.02 | 82.3 | 761668.9 | 730756.72 | 24.26 | 1269.388 | 3158.712 | 752.913 | 73 | 170 | 35.9 | 46.5 | 35.6 | 47 | 0 | 0 | - | - | 39.3 | 41.6 | 242 | 193 | 64.1 | 64.1 | 72.6 | 25.9 | 44.9 | 2.61 | 11.3 | 26.2 | 64.2 | 76.9 | 25.7 | 48 | 2.83 | 10.9 | 27.8 | 23.7 | 25.5 | 35.4 | 2.75 | 1.13 | 2.89 | 1.13 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:20:00 | 3088.48 | 82.3 | 761730.92 | 730756.72 | 25.09 | 1195.584 | 3232.512 | 754.092 | 74 | 170 | 35.9 | 46.5 | 35.5 | 47.1 | 0 | 0 | - | - | 39.2 | 41.7 | 242 | 193 | 66.2 | 65.9 | 73.3 | 25.7 | 46 | 2.67 | 11.3 | 26 | 65.8 | 77.1 | 25.6 | 48.4 | 2.86 | 11.2 | 27.5 | 23.6 | 25.4 | 35.6 | 2.71 | 1.13 | 2.87 | 1.13 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:25:00 | 3151.42 | 82.3 | 761794.18 | 730756.72 | 25.89 | 1136.544 | 3291.552 | 752.045 | 76 | 170 | 35.7 | 46.8 | 35.7 | 46.9 | 0 | 0 | - | - | 39.2 | 41.7 | 242 | 193 | 64 | 63.5 | 73.1 | 25.7 | 45.4 | 2.61 | 11.1 | 26.7 | 63.5 | 77 | 25.5 | 47.9 | 2.81 | 10.9 | 28.1 | 23.3 | 25.2 | 33.7 | 2.6 | 1.12 | 2.81 | 1.13 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:30:00 | 3221.32 | 82.3 | 761863.68 | 730756.72 | 26.7 | 1055.363 | 3372.738 | 951.487 | 77 | 170 | 35.4 | 47 | 35.6 | 46.9 | 0 | 0 | - | - | 39.1 | 41.8 | 242 | 193 | 62.2 | 62.2 | 71.1 | 25.4 | 43.9 | 2.54 | 11.2 | 25.8 | 62.4 | 75.7 | 25.2 | 47.2 | 2.77 | 10.8 | 27.5 | 23.2 | 25.1 | 34.2 | 2.65 | 1.11 | 2.81 | 1.12 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:35:00 | 3305.62 | 82.3 | 761948.78 | 730756.72 | 27.52 | 974.178 | 3453.918 | 1132.207 | 79 | 170 | 35.4 | 47 | 35.2 | 47.4 | 0 | 0 | - | - | 38.9 | 42 | 242 | 193 | 62.1 | 62.2 | 71.3 | 25.2 | 44.3 | 2.54 | 10.9 | 25.9 | 62.2 | 75.7 | 25.1 | 47.1 | 2.76 | 10.7 | 27.6 | 23.1 | 24.8 | 33.4 | 2.63 | 1.12 | 2.78 | 1.12 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:40:00 | 3400.28 | 82.3 | 762043.34 | 730756.72 | 28.32 | 878.238 | 3549.859 | 1104.507 | 82 | 170 | 35.4 | 46.9 | 34.8 | 47.9 | 0 | 0 | - | - | 38.8 | 42.1 | 242 | 193 | 61.3 | 61.3 | 71.2 | 25.1 | 44.2 | 2.55 | 11 | 25.7 | 61.2 | 75.2 | 24.9 | 46.8 | 2.75 | 10.7 | 27.3 | 22.9 | 24.8 | 32.9 | 2.61 | 1.12 | 2.76 | 1.12 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:45:00 | 3494.78 | 82.3 | 762137.26 | 730756.72 | 29.12 | 767.535 | 3660.564 | 1117.185 | 84 | 170 | 35.3 | 47 | 34.5 | 48.3 | 0 | 0 | - | - | 38.5 | 42.4 | 242 | 193 | 60.2 | 60.2 | 70.9 | 24.9 | 43.9 | 2.54 | 10.8 | 25.6 | 60.2 | 74.7 | 24.8 | 46.5 | 2.72 | 10.7 | 27.3 | 22.8 | 24.7 | 32.7 | 2.61 | 1.12 | 2.76 | 1.12 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:50:00 | 3581.62 | 82.3 | 762224.08 | 730756.72 | 29.9 | 664.212 | 3763.884 | 743.541 | 86 | 170 | 35.2 | 47.1 | 34.1 | 48.6 | 0 | 0 | - | - | 38.3 | 42.6 | 242 | 193 | 60.2 | 60.2 | 70.9 | 24.8 | 43.8 | 2.53 | 10.8 | 25.8 | 60.2 | 74.7 | 24.7 | 46.4 | 2.71 | 10.6 | 27.3 | 22.7 | 24.6 | 32.9 | 2.58 | 1.12 | 2.74 | 1.11 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 13:55:00 | 3612.7 | 82.42 | 762253.98 | 730756.86 | 30.65 | 649.452 | 3778.644 | -11.702 | 86 | 170 | 34.9 | 47.4 | 33.9 | 49 | 0 | 0 | - | - | 38 | 42.9 | 242 | 193 | 59.5 | 59.1 | 70.4 | 24.7 | 43.4 | 2.48 | 10.7 | 26 | 59.2 | 74.2 | 24.7 | 46.2 | 2.69 | 10.5 | 27.1 | 22.6 | 24.4 | 33.3 | 2.53 | 1.11 | 2.71 | 1.12 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:00:00 | 3612.7 | 83.48 | 762253.98 | 730757.9 | 31.39 | 649.452 | 3778.644 | -14.124 | 86 | 170 | 34.5 | 47.8 | 33.6 | 49.3 | 0 | 0 | - | - | 37.6 | 43.2 | 242 | 193 | 58.1 | 57.9 | 69.1 | 24.7 | 42.6 | 2.45 | 10.7 | 25.2 | 58.2 | 73.3 | 24.4 | 45.6 | 2.66 | 10.4 | 26.7 | 22.3 | 24.2 | 32.3 | 2.48 | 1.11 | 2.67 | 1.12 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:05:00 | 3623.38 | 83.7 | 762264.88 | 730758.12 | 32.13 | 619.932 | 3808.164 | 161.602 | 87 | 170 | 34.1 | 48.2 | 33.1 | 49.7 | 0 | 0 | - | - | 37.1 | 43.6 | 242 | 193 | 56.7 | 56.6 | 67.9 | 24.4 | 41.7 | 2.4 | 10.6 | 24.7 | 56.6 | 72.5 | 24.2 | 45.1 | 2.63 | 10.2 | 26.3 | 22.1 | 23.9 | 31.8 | 2.45 | 1.1 | 2.64 | 1.11 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:10:00 | 3637.32 | 83.7 | 762278.84 | 730758.12 | 32.85 | 612.552 | 3815.545 | 165.881 | 87 | 170 | 33.7 | 48.5 | 32.7 | 50.1 | 0 | 0 | - | - | 36.6 | 44.1 | 242 | 193 | 55.7 | 55.5 | 67.1 | 24.2 | 41.1 | 2.36 | 10.5 | 24.7 | 55.6 | 71.3 | 24 | 44.6 | 2.59 | 10.2 | 25.8 | 21.8 | 23.7 | 31.3 | 2.44 | 1.09 | 2.62 | 1.1 | 242 | 193 | 2554 | 2554
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:15:00 | 3651.26 | 83.7 | 762293.08 | 730758.12 | 33.56 | 605.172 | 3822.926 | 367.911 | 87 | 170 | 33.4 | 48.8 | 32.3 | 50.6 | 0 | 0 | - | - | 36.1 | 44.6 | 242 | 193 | 55.1 | 55.2 | 66.9 | 23.9 | 41 | 2.36 | 10.6 | 24.4 | 55.1 | 71.2 | 23.7 | 44.4 | 2.58 | 10.1 | 25.8 | 21.7 | 23.5 | 31.3 | 2.45 | 1.09 | 2.61 | 1.1 | 242 | 193 | 2491 | 2490
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:20:00 | 3681.78 | 83.7 | 762324.08 | 730758.12 | 34.24 | 560.892 | 3867.21 | 370.177 | 88 | 170 | 32.9 | 49.3 | 31.9 | 51 | 0 | 0 | - | - | 35.6 | 45.2 | 242 | 193 | 54.3 | 54.3 | 66.7 | 23.7 | 40.9 | 2.35 | 10.2 | 24.3 | 54.1 | 70.9 | 23.6 | 44 | 2.56 | 9.9 | 25.9 | 21.7 | 23.4 | 30.7 | 2.37 | 1.1 | 2.55 | 1.1 | 242 | 193 | 2361 | 2359
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:25:00 | 3712.64 | 83.7 | 762354.28 | 730758.12 | 34.89 | 538.751 | 3889.35 | 380.153 | 89 | 170 | 32.3 | 49.9 | 31.4 | 51.5 | 0 | 0 | - | - | 35.1 | 45.7 | 242 | 193 | 51.9 | 51.6 | 65.1 | 23.7 | 39.9 | 2.29 | 10.2 | 23.8 | 52 | 69.5 | 23.5 | 43.2 | 2.51 | 9.9 | 25.4 | 21.6 | 23.3 | 29.3 | 2.37 | 1.09 | 2.52 | 1.09 | 242 | 193 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:30:00 | 3743 | 83.7 | 762384.86 | 730758.12 | 35.54 | 516.61 | 3911.49 | 362.28 | 89 | 170 | 31.9 | 50.4 | 31 | 52 | 0 | 0 | - | - | 34.5 | 46.3 | 242 | 193 | 51 | 51.1 | 64.8 | 23.4 | 39.7 | 2.28 | 10.2 | 23.6 | 51 | 68.9 | 23.3 | 42.7 | 2.48 | 10 | 25.2 | 21.3 | 23.1 | 28.3 | 2.35 | 1.08 | 2.51 | 1.09 | 242 | 193 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:35:00 | 3780.68 | 83.7 | 762422.82 | 730758.12 | 36.19 | 472.326 | 3955.77 | 542.462 | 90 | 170 | 31.6 | 50.7 | 30.6 | 52.3 | 0 | 0 | - | - | 34 | 46.7 | 242 | 193 | 50.5 | 50.6 | 64.4 | 23.2 | 39.4 | 2.26 | 10.1 | 23.5 | 50.5 | 68.5 | 23.2 | 42.5 | 2.46 | 9.9 | 25.1 | 21.1 | 22.9 | 27.4 | 2.34 | 1.08 | 2.49 | 1.08 | 242 | 193 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:40:00 | 3825.96 | 83.7 | 762467.88 | 730758.12 | 36.85 | 420.666 | 4007.43 | 539.917 | 91 | 170 | 31.2 | 51.1 | 30.2 | 52.7 | 0 | 0 | - | - | 33.5 | 47.3 | 242 | 193 | 50 | 50.1 | 64 | 23 | 39.2 | 2.26 | 10.1 | 23.3 | 50 | 68.2 | 22.9 | 42.2 | 2.45 | 9.8 | 24.9 | 20.9 | 22.7 | 27.2 | 2.36 | 1.07 | 2.49 | 1.07 | 242 | 193 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:45:00 | 3871.4 | 83.7 | 762513.76 | 730758.12 | 37.51 | 376.386 | 4051.71 | 540.607 | 92 | 170 | 30.9 | 51.5 | 29.8 | 53.1 | 0 | 0 | - | - | 33 | 47.8 | 242 | 193 | 50.6 | 50.1 | 64.6 | 22.8 | 39.6 | 2.28 | 10 | 23.5 | 50.5 | 68.3 | 22.7 | 42.3 | 2.46 | 9.9 | 25 | 20.8 | 22.6 | 27.3 | 2.37 | 1.07 | 2.5 | 1.07 | 242 | 193 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:50:00 | 3914.14 | 83.7 | 762556.08 | 730758.12 | 38.16 | 317.346 | 4110.755 | 324.975 | 93 | 170 | 30.5 | 51.8 | 29.4 | 53.6 | 0 | 0 | - | - | 32.6 | 48.2 | 242 | 193 | 50.6 | 51.1 | 65 | 22.7 | 39.8 | 2.29 | 10 | 23.6 | 51 | 68.5 | 22.6 | 42.4 | 2.46 | 9.9 | 25.1 | 20.7 | 22.4 | 27.7 | 2.37 | 1.07 | 2.5 | 1.07 | 242 | 193 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 14:55:00 | 3940 | 83.7 | 762581.6 | 730758.12 | 38.78 | 265.686 | 4162.416 | 336.081 | 94 | 170 | 30.1 | 52.2 | 29.1 | 54.1 | 0 | 0 | - | - | 32.3 | 48.5 | 242 | 193 | 51.1 | 51.1 | 65 | 22.6 | 39.9 | 2.3 | 9.9 | 23.5 | 51 | 68.6 | 22.4 | 42.4 | 2.46 | 9.9 | 25.1 | 20.6 | 22.3 | 28.2 | 2.36 | 1.06 | 2.5 | 1.06 | 242 | 193 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:00:00 | 3948.36 | 84.1 | 762589.64 | 730758.52 | 39.44 | 265.686 | 4162.416 | 13.906 | 94 | 170 | 29.6 | 52.7 | 28.8 | 54.5 | 0 | 0 | - | - | 32 | 48.9 | 242 | 193 | 51.3 | 51 | 64.9 | 22.3 | 39.6 | 2.27 | 10 | 24 | 51 | 68.7 | 22.3 | 42.4 | 2.47 | 9.9 | 25.2 | 20.3 | 22.2 | 28.1 | 2.35 | 1.05 | 2.52 | 1.06 | 242 | 193 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:05:00 | 3948.52 | 84.78 | 762589.8 | 730759.22 | 40.07 | 265.686 | 4162.416 | -15.028 | 94 | 170 | 29.1 | 53.3 | 28.3 | 55 | 0 | 0 | - | - | 31.8 | 49 | 242 | 193 | 51.9 | 52 | 64.9 | 22.2 | 39.5 | 2.28 | 10.1 | 23.8 | 52 | 68.9 | 22.2 | 42.6 | 2.48 | 9.8 | 25.3 | 20.2 | 21.9 | 27.5 | 2.34 | 1.04 | 2.5 | 1.05 | 242 | 193 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:10:00 | 3948.52 | 85.82 | 762589.8 | 730760.26 | 40.73 | 265.686 | 4162.416 | -12.54 | 94 | 170 | 28.8 | 53.8 | 28.1 | 55.2 | 0 | 0 | - | - | 31.6 | 49.2 | 242 | 193 | 51.7 | 51.8 | 64.6 | 22.1 | 39.3 | 2.26 | 10.1 | 23.9 | 51.7 | 68.9 | 21.9 | 42.4 | 2.46 | 9.8 | 25.5 | 19.9 | 21.7 | 27.7 | 2.35 | 1.03 | 2.53 | 1.04 | 242 | 193 | 2499 | 2499
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:15:00 | 3948.52 | 86.88 | 762589.8 | 730761.3 | 41.44 | 265.686 | 4162.416 | -12.608 | 94 | 170 | 28.6 | 53.7 | 28 | 55 | 0 | 0 | - | - | 31.4 | 49.3 | 242 | 193 | 53.4 | 53.5 | 65.4 | 21.8 | 39.5 | 2.28 | 10.5 | 24.4 | 53.2 | 69.5 | 21.7 | 42.8 | 2.5 | 10.1 | 25.5 | 19.6 | 21.3 | 27.5 | 2.37 | 1.02 | 2.55 | 1.03 | 242 | 193 | 2652 | 2652
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:20:00 | 3948.54 | 87.88 | 762589.82 | 730762.32 | 42.15 | 265.686 | 4162.416 | -30.453 | 94 | 170 | 28.5 | 53.8 | 28 | 55 | 0 | 0 | - | - | 31.2 | 49.5 | 242 | 193 | 53.8 | 54 | 66.1 | 21.4 | 39.7 | 2.28 | 10.1 | 25.1 | 53.8 | 70.4 | 21.3 | 43 | 2.5 | 9.9 | 26.4 | 19.2 | 21.1 | 27.5 | 2.4 | 1.02 | 2.55 | 1.02 | 242 | 193 | 2628 | 2628
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:25:00 | 3948.54 | 88.98 | 762589.82 | 730763.4 | 42.9 | 265.686 | 4162.416 | -10.513 | 94 | 170 | 28.3 | 53.8 | 27.9 | 54.9 | 0 | 0 | - | - | 31.1 | 49.5 | 242 | 193 | 54.2 | 54.9 | 66.5 | 21.1 | 40.3 | 2.33 | 10.2 | 24.6 | 54.3 | 70.5 | 21.1 | 43.2 | 2.52 | 9.8 | 26.1 | 18.9 | 20.7 | 27.8 | 2.39 | 1 | 2.55 | 1.01 | 242 | 193 | 2632 | 2632
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:30:00 | 3948.62 | 90.06 | 762589.9 | 730764.52 | 43.63 | 265.686 | 4162.416 | -23.308 | 94 | 170 | 28.3 | 53.7 | 27.8 | 54.8 | 0 | 0 | - | - | 31 | 49.6 | 242 | 193 | 54.7 | 55 | 66.8 | 20.9 | 40.1 | 2.31 | 10.2 | 25.2 | 54.8 | 70.7 | 20.7 | 43.2 | 2.51 | 9.8 | 26.5 | 18.7 | 20.6 | 28.8 | 2.38 | 1 | 2.54 | 1.01 | 242 | 193 | 2652 | 2652
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:35:00 | 3948.64 | 91.04 | 762589.92 | 730765.48 | 44.36 | 265.686 | 4162.416 | -15.952 | 94 | 170 | 28.3 | 53.4 | 27.6 | 54.7 | 0 | 0 | - | - | 30.9 | 49.6 | 242 | 193 | 54 | 54.1 | 66.6 | 20.7 | 39.9 | 2.3 | 10 | 25.2 | 54.3 | 70.7 | 20.6 | 42.9 | 2.49 | 9.7 | 26.7 | 18.4 | 20.2 | 29.7 | 2.38 | 0.99 | 2.53 | 1 | 242 | 193 | 2677 | 2677
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:40:00 | 3948.64 | 92.02 | 762589.92 | 730766.44 | 45.1 | 265.686 | 4162.416 | -10.997 | 94 | 170 | 28.3 | 53.1 | 27.4 | 54.7 | 0 | 0 | - | - | 30.8 | 49.5 | 242 | 193 | 54.1 | 54 | 66.6 | 20.4 | 39.9 | 2.3 | 10.1 | 25.2 | 53.8 | 70.4 | 20.2 | 42.7 | 2.49 | 9.7 | 26.5 | 18.2 | 20 | 28.8 | 2.42 | 0.99 | 2.54 | 0.99 | 242 | 193 | 2722 | 2722
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:45:00 | 3948.64 | 92.78 | 762589.92 | 730767.22 | 45.86 | 265.686 | 4162.416 | -11.461 | 94 | 170 | 28.2 | 53 | 27.3 | 54.7 | 0 | 0 | - | - | 30.8 | 49.4 | 242 | 193 | 54.9 | 54.9 | 67.1 | 20.2 | 40.5 | 2.33 | 10 | 25.2 | 54.9 | 70.8 | 19.9 | 43 | 2.51 | 9.7 | 26.6 | 17.9 | 19.7 | 29.2 | 2.39 | 0.98 | 2.54 | 0.98 | 242 | 193 | 2727 | 2727
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:50:00 | 3948.64 | 93.78 | 762589.92 | 730768.26 | 46.61 | 265.686 | 4162.416 | -8.449 | 94 | 170 | 28.1 | 52.9 | 27.1 | 54.6 | 0 | 0 | - | - | 30.8 | 49.3 | 242 | 193 | 55 | 54.9 | 67.4 | 19.9 | 40.1 | 2.3 | 10 | 25.9 | 54.9 | 71 | 19.7 | 43.1 | 2.5 | 9.7 | 27 | 17.7 | 19.6 | 29.7 | 2.4 | 0.97 | 2.54 | 0.98 | 242 | 193 | 2751 | 2757
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 15:55:00 | 3948.64 | 94.9 | 762589.92 | 730769.34 | 47.37 | 265.686 | 4162.416 | -14.428 | 94 | 170 | 27.9 | 52.9 | 27 | 54.6 | 0 | 0 | - | - | 30.7 | 49.2 | 242 | 193 | 54.9 | 54.8 | 67.4 | 19.7 | 40.1 | 2.31 | 10 | 25.7 | 54.9 | 70.9 | 19.6 | 42.9 | 2.49 | 9.7 | 27 | 17.4 | 19.2 | 29.8 | 2.39 | 0.97 | 2.54 | 0.97 | 242 | 193 | 2766 | 2766
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:00:00 | 3948.66 | 95.8 | 762589.94 | 730770.26 | 47.88 | 265.686 | 4162.416 | -13.095 | 94 | 170 | 27.8 | 52.8 | 26.8 | 54.6 | 0 | 0 | - | - | 30.7 | 49 | 242 | 193 | 55.1 | 55.6 | 67.4 | 19.4 | 40.1 | 2.31 | 10.1 | 25.8 | 55.4 | 71 | 19.2 | 42.9 | 2.5 | 9.7 | 27 | 19.7 | 19.6 | 28.9 | 1.73 | 0.88 | 1.8 | 1.08 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:05:00 | 3948.66 | 96.82 | 762589.94 | 730771.28 | 48 | 265.686 | 4162.416 | -11.247 | 94 | 170 | 27.6 | 53.3 | 26.7 | 55 | 0 | 0 | - | - | 30.7 | 48.9 | 0 | 0 | 0 | 0 | 55.1 | 22.2 | 31.7 | 1.63 | 4.9 | 27.4 | 0 | 52.9 | 24.3 | 33.2 | 1.72 | 4.1 | 24.1 | 22.1 | 21.9 | 28.6 | 1.47 | 1.42 | 1.5 | 1.43 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:10:00 | 3948.66 | 97.88 | 762589.94 | 730772.3 | 48.12 | 265.686 | 4162.416 | -11.544 | 94 | 170 | 27.3 | 54 | 26.7 | 55.4 | 0 | 0 | - | - | 30.6 | 48.8 | 0 | 0 | 0 | 0 | 30.7 | 36.3 | 29.3 | 1.42 | 14.1 | 7.7 | 0 | 30.2 | 38.8 | 29.3 | 1.47 | 16.3 | 6.6 | 22.9 | 22.7 | 27.9 | 1.46 | 1.45 | 1.44 | 1.46 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:15:00 | 3948.66 | 98.86 | 762589.94 | 730773.28 | 48.23 | 265.686 | 4162.416 | -15.539 | 94 | 170 | 27.1 | 54.4 | 26.6 | 55.6 | 0 | 0 | - | - | 30.6 | 48.7 | 0 | 0 | 0 | 0 | 28.9 | 36.9 | 29.1 | 1.43 | 13.9 | 5.7 | 0 | 28.6 | 39.9 | 28.8 | 1.44 | 16.8 | 5.8 | 23.3 | 23 | 27.7 | 1.47 | 1.47 | 1.46 | 1.47 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:20:00 | 3948.66 | 99.86 | 762589.94 | 730774.32 | 48.34 | 265.686 | 4162.416 | -12.205 | 94 | 170 | 27 | 54.8 | 26.6 | 55.7 | 0 | 0 | - | - | 30.5 | 48.8 | 0 | 0 | 0 | 0 | 28.7 | 36.6 | 28.9 | 1.44 | 13.2 | 5.2 | 0 | 29 | 38.1 | 28.6 | 1.45 | 14.7 | 6 | 23.4 | 23.2 | 27.8 | 1.48 | 1.47 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:25:00 | 3948.74 | 100.98 | 762590.02 | 730775.42 | 48.45 | 280.446 | 4147.656 | -9.459 | 94 | 170 | 26.9 | 55 | 26.5 | 55.8 | 0 | 0 | - | - | 30.5 | 48.8 | 0 | 0 | 0 | 0 | 28.7 | 35.7 | 28.7 | 1.45 | 12.3 | 5.1 | 0 | 29.2 | 36.6 | 28.3 | 1.45 | 13 | 6 | 23.5 | 23.3 | 27.8 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:30:00 | 3948.76 | 101.94 | 762590.04 | 730776.4 | 48.55 | 265.686 | 4162.416 | -13.822 | 94 | 170 | 26.8 | 55.1 | 26.5 | 55.9 | 0 | 0 | - | - | 30.5 | 48.8 | 0 | 0 | 0 | 0 | 28.7 | 35.8 | 28.7 | 1.45 | 12.3 | 4.9 | 0 | 29.2 | 35.9 | 28.2 | 1.46 | 12.1 | 5.9 | 23.6 | 23.4 | 27.8 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:35:00 | 3948.76 | 103.02 | 762590.04 | 730777.44 | 48.64 | 287.826 | 4140.276 | -12.718 | 94 | 170 | 26.7 | 55.2 | 26.4 | 56 | 0 | 0 | - | - | 30.4 | 48.8 | 0 | 0 | 0 | 0 | 28.7 | 35.4 | 28.6 | 1.45 | 11.8 | 4.8 | 0 | 29.1 | 35.2 | 28.1 | 1.46 | 11.5 | 5.7 | 23.6 | 23.4 | 27.8 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:40:00 | 3948.76 | 104.02 | 762590.04 | 730778.46 | 48.74 | 287.826 | 4140.276 | -14.043 | 94 | 170 | 26.7 | 55.3 | 26.4 | 56 | 0 | 0 | - | - | 30.4 | 48.8 | 0 | 0 | 0 | 0 | 28.6 | 35.1 | 28.4 | 1.46 | 11.5 | 4.7 | 0 | 28.9 | 34.9 | 28.1 | 1.46 | 10.9 | 5.5 | 23.6 | 23.4 | 27.7 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:45:00 | 3948.76 | 105.02 | 762590.04 | 730779.46 | 48.82 | 287.826 | 4140.276 | -12.782 | 94 | 170 | 26.6 | 55.3 | 26.4 | 56 | 0 | 0 | - | - | 30.3 | 48.8 | 0 | 0 | 0 | 0 | 28.4 | 34.9 | 28.3 | 1.46 | 11.2 | 4.5 | 0 | 28.7 | 34.2 | 27.9 | 1.46 | 10.4 | 5.2 | 23.7 | 23.5 | 27.4 | 1.49 | 1.49 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:50:00 | 3948.76 | 106.72 | 762590.04 | 730781.56 | 48.91 | 309.966 | 4118.136 | -221.326 | 93 | 170 | 26.6 | 55.4 | 26.3 | 56.1 | 0 | 0 | - | - | 30.3 | 48.9 | 0 | 0 | 0 | 0 | 28.2 | 35.1 | 28.2 | 1.46 | 11.3 | 4.3 | 0 | 28.6 | 33.7 | 27.8 | 1.46 | 9.9 | 5.1 | 23.7 | 23.5 | 27.4 | 1.49 | 1.49 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 16:55:00 | 3948.76 | 130.18 | 762590.04 | 730805.26 | 49.01 | 317.346 | 4110.755 | -439.407 | 93 | 170 | 26.6 | 55.4 | 26.3 | 56.2 | 0 | 0 | - | - | 30.2 | 48.9 | 0 | 0 | 0 | 0 | 28.1 | 34.6 | 28.1 | 1.46 | 10.9 | 4.2 | 0 | 28.3 | 33.2 | 27.7 | 1.46 | 9.3 | 4.9 | 23.7 | 23.5 | 27.3 | 1.49 | 1.49 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:00:00 | 3948.76 | 192.48 | 762590.04 | 730868.7 | 49.11 | 435.426 | 3992.671 | -849.129 | 91 | 170 | 26.5 | 55.5 | 26.3 | 56.2 | 0 | 0 | - | - | 30.2 | 48.9 | 0 | 0 | 0 | 0 | 27.9 | 34.2 | 27.9 | 1.46 | 10.4 | 4 | 0 | 28.2 | 32.7 | 27.7 | 1.46 | 8.8 | 4.7 | 23.7 | 23.5 | 27.3 | 1.49 | 1.49 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:05:00 | 3948.76 | 264.16 | 762590.04 | 730939.94 | 49.21 | 516.61 | 3911.49 | -877.349 | 90 | 170 | 26.5 | 55.6 | 26.3 | 56.2 | 0 | 0 | - | - | 30.1 | 48.9 | 0 | 0 | 0 | 0 | 27.9 | 33.9 | 27.9 | 1.46 | 10.1 | 4 | 0 | 28.1 | 32.4 | 27.7 | 1.46 | 8.5 | 4.6 | 23.8 | 23.6 | 27.4 | 1.5 | 1.49 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:10:00 | 3948.76 | 334 | 762590.04 | 731010.2 | 49.31 | 605.172 | 3822.926 | -855.573 | 88 | 170 | 26.5 | 55.6 | 26.3 | 56.2 | 0 | 0 | - | - | 30.1 | 49 | 0 | 0 | 0 | 0 | 27.9 | 33.4 | 27.8 | 1.46 | 9.6 | 3.9 | 0 | 28 | 32.1 | 27.6 | 1.47 | 8.1 | 4.4 | 23.9 | 23.7 | 27.3 | 1.5 | 1.49 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:15:00 | 3948.76 | 406.56 | 762590.04 | 731081.88 | 49.41 | 656.832 | 3771.264 | -847.576 | 86 | 170 | 26.5 | 55.6 | 26.4 | 56.1 | 0 | 0 | - | - | 30 | 49 | 0 | 0 | 0 | 0 | 27.9 | 32.9 | 27.8 | 1.46 | 9 | 3.9 | 0 | 27.9 | 31.8 | 27.6 | 1.47 | 7.7 | 4.3 | 23.9 | 23.7 | 27.3 | 1.5 | 1.5 | 1.49 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:20:00 | 3948.76 | 476.28 | 762590.04 | 731151.58 | 49.52 | 745.392 | 3682.704 | -852.725 | 85 | 170 | 26.6 | 55.7 | 26.4 | 56.1 | 0 | 0 | - | - | 30 | 49 | 0 | 0 | 0 | 0 | 27.9 | 32.4 | 27.8 | 1.47 | 8.4 | 3.8 | 0 | 27.9 | 31.4 | 27.6 | 1.47 | 7.3 | 4.2 | 24 | 23.8 | 27.3 | 1.51 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:25:00 | 3948.76 | 549.04 | 762590.04 | 731224.32 | 49.63 | 841.338 | 3586.758 | -854.356 | 83 | 170 | 26.6 | 55.6 | 26.5 | 56 | 0 | 0 | - | - | 30 | 49 | 0 | 0 | 0 | 0 | 28 | 31.9 | 27.8 | 1.47 | 7.8 | 3.8 | 0 | 27.9 | 31.1 | 27.6 | 1.48 | 6.8 | 4.1 | 24.1 | 24 | 27.3 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:30:00 | 3948.76 | 618.9 | 762590.04 | 731294.18 | 49.74 | 892.998 | 3535.099 | -851.542 | 81 | 170 | 26.6 | 55.7 | 26.6 | 55.9 | 0 | 0 | - | - | 30 | 49.1 | 0 | 0 | 0 | 0 | 28 | 31.4 | 27.9 | 1.48 | 7.2 | 3.7 | 0 | 27.9 | 30.7 | 27.7 | 1.48 | 6.3 | 3.9 | 24.3 | 24.1 | 27.6 | 1.52 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:35:00 | 3948.76 | 688.76 | 762590.04 | 731364.46 | 49.85 | 974.178 | 3453.918 | -851.61 | 80 | 170 | 26.6 | 55.7 | 26.5 | 56 | 0 | 0 | - | - | 30 | 49.1 | 0 | 0 | 0 | 0 | 28.2 | 31.1 | 27.9 | 1.48 | 6.7 | 3.7 | 0 | 27.9 | 30.3 | 27.7 | 1.49 | 5.9 | 3.8 | 24.4 | 24.2 | 27.8 | 1.52 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:40:00 | 3948.76 | 761.3 | 762590.04 | 731437.54 | 49.96 | 1047.982 | 3380.118 | -849.742 | 78 | 170 | 26.6 | 55.7 | 26.4 | 56.3 | 0 | 0 | - | - | 30 | 49.1 | 0 | 0 | 0 | 0 | 28.6 | 30.9 | 28.5 | 1.48 | 6.5 | 4 | 0 | 28.2 | 30.2 | 27.8 | 1.49 | 5.6 | 4.1 | 24.5 | 24.3 | 27.8 | 1.53 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:45:00 | 3948.76 | 831.82 | 762590.04 | 731507.16 | 50.07 | 1114.404 | 3313.692 | -852.679 | 76 | 170 | 26.7 | 55.7 | 26.6 | 56.1 | 0 | 0 | - | - | 30 | 49 | 0 | 0 | 0 | 0 | 28.8 | 30.8 | 28.7 | 1.49 | 6.2 | 4.1 | 0 | 28.3 | 30.2 | 28 | 1.5 | 5.4 | 4 | 24.6 | 24.4 | 27.6 | 1.53 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:50:00 | 3948.76 | 902.8 | 762590.04 | 731578.56 | 50.19 | 1202.964 | 3225.132 | -867.171 | 75 | 170 | 26.7 | 55.7 | 26.8 | 55.8 | 0 | 0 | - | - | 30 | 49 | 0 | 0 | 0 | 0 | 28.8 | 30.6 | 28.6 | 1.5 | 5.8 | 4 | 0 | 28.3 | 29.9 | 28.1 | 1.5 | 5.1 | 3.9 | 24.7 | 24.5 | 27.4 | 1.54 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 17:55:00 | 3948.76 | 974.34 | 762590.04 | 731649.62 | 50.3 | 1262.007 | 3166.092 | -860.011 | 73 | 170 | 26.7 | 55.8 | 26.9 | 55.7 | 0 | 0 | - | - | 30 | 49.1 | 0 | 0 | 0 | 0 | 28.8 | 30.2 | 28.4 | 1.5 | 5.4 | 3.8 | 0 | 28.3 | 29.8 | 28.1 | 1.5 | 4.9 | 3.8 | 24.8 | 24.7 | 27.9 | 1.54 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:00:00 | 3948.76 | 1044.1 | 762590.04 | 731719.88 | 50.42 | 1357.95 | 3070.148 | -852.763 | 71 | 170 | 26.8 | 55.8 | 27 | 55.6 | 0 | 0 | - | - | 30 | 49 | 0 | 0 | 0 | 0 | 28.9 | 30.1 | 28.6 | 1.5 | 5.2 | 3.9 | 0 | 28.4 | 29.7 | 28.2 | 1.51 | 4.7 | 3.8 | 24.9 | 24.8 | 27.8 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:05:00 | 3948.76 | 1114.56 | 762590.04 | 731791.68 | 50.54 | 1439.13 | 2988.966 | -851.552 | 69 | 170 | 26.8 | 55.8 | 27.1 | 55.6 | 0 | 0 | - | - | 30 | 49 | 0 | 0 | 0 | 0 | 29.3 | 30.1 | 29 | 1.5 | 5.3 | 4.4 | 0 | 28.6 | 29.8 | 28.3 | 1.51 | 4.7 | 3.9 | 25.1 | 24.9 | 27.7 | 1.54 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:10:00 | 3948.76 | 1186.8 | 762590.04 | 731862.58 | 50.66 | 1498.171 | 2929.926 | -849.758 | 68 | 170 | 26.8 | 55.8 | 27.1 | 55.5 | 0 | 0 | - | - | 30.1 | 49.1 | 0 | 0 | 0 | 0 | 29.6 | 30.1 | 29.3 | 1.5 | 5.2 | 4.5 | 0 | 28.8 | 29.8 | 28.3 | 1.51 | 4.7 | 4.1 | 25.1 | 25 | 27.7 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:15:00 | 3948.76 | 1258.42 | 762590.04 | 731933.68 | 50.77 | 1579.356 | 2848.746 | -833.256 | 66 | 170 | 26.9 | 55.9 | 27.2 | 55.5 | 0 | 0 | - | - | 30 | 49.1 | 0 | 0 | 0 | 0 | 29.7 | 30.1 | 29.2 | 1.51 | 5.1 | 4.6 | 0 | 28.9 | 29.8 | 28.4 | 1.52 | 4.6 | 4.1 | 25.2 | 25 | 27.7 | 1.55 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:20:00 | 3948.76 | 1328 | 762590.04 | 732003.24 | 50.9 | 1645.776 | 2782.32 | -854.46 | 64 | 170 | 26.9 | 56 | 27.2 | 55.5 | 0 | 0 | - | - | 30 | 49.1 | 0 | 0 | 0 | 0 | 29.7 | 30.1 | 29.2 | 1.51 | 5 | 4.5 | 0 | 28.9 | 29.7 | 28.4 | 1.52 | 4.4 | 4 | 25.2 | 25 | 27.5 | 1.55 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:25:00 | 3948.76 | 1398.94 | 762590.04 | 732074.68 | 51.02 | 1734.336 | 2693.76 | -850.846 | 63 | 170 | 26.9 | 56 | 27.3 | 55.4 | 0 | 0 | - | - | 30 | 49.2 | 0 | 0 | 0 | 0 | 29.7 | 30.1 | 29.1 | 1.51 | 4.9 | 4.4 | 0 | 28.9 | 29.7 | 28.3 | 1.53 | 4.3 | 4 | 25.3 | 25.1 | 27.4 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:30:00 | 3948.76 | 1470.16 | 762590.04 | 732145.88 | 51.15 | 1808.141 | 2619.96 | -851.404 | 61 | 170 | 26.9 | 56 | 27.3 | 55.4 | 0 | 0 | - | - | 30 | 49.2 | 0 | 0 | 0 | 0 | 29.6 | 30.1 | 28.9 | 1.51 | 4.8 | 4.3 | 0 | 28.8 | 29.7 | 28.3 | 1.52 | 4.3 | 3.9 | 25.2 | 25.1 | 27.3 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:35:00 | 3948.76 | 1539.36 | 762590.04 | 732216.72 | 51.27 | 1896.702 | 2531.395 | -1061.76 | 59 | 170 | 26.9 | 56.1 | 27.4 | 55.4 | 0 | 0 | - | - | 30 | 49.3 | 0 | 0 | 0 | 0 | 29.4 | 29.9 | 28.7 | 1.51 | 4.8 | 4.1 | 0 | 28.7 | 29.6 | 28.2 | 1.52 | 4.2 | 3.8 | 25.2 | 25.1 | 27.4 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:40:00 | 3948.76 | 1628.7 | 762590.04 | 732304.84 | 51.4 | 1992.642 | 2435.454 | -1086.077 | 57 | 170 | 26.9 | 56.1 | 27.4 | 55.4 | 0 | 0 | - | - | 29.9 | 49.3 | 0 | 0 | 0 | 0 | 29.4 | 30 | 28.8 | 1.52 | 4.8 | 4.1 | 0 | 28.8 | 29.6 | 28.2 | 1.52 | 4.1 | 3.8 | 25.2 | 25.1 | 27.4 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:45:00 | 3948.76 | 1718.32 | 762590.04 | 732392.74 | 51.53 | 2088.587 | 2339.512 | -1084.514 | 55 | 170 | 26.9 | 56.1 | 27.5 | 55.4 | 0 | 0 | - | - | 29.9 | 49.5 | 0 | 0 | 0 | 0 | 29.5 | 30.1 | 28.9 | 1.52 | 4.9 | 4.2 | 0 | 28.8 | 29.6 | 28.2 | 1.53 | 4.1 | 3.8 | 25.2 | 25.1 | 27.2 | 1.56 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:50:00 | 3948.76 | 1808.9 | 762590.04 | 732485.24 | 51.67 | 2206.668 | 2221.428 | -1272.209 | 53 | 170 | 27 | 56.1 | 27.6 | 55.3 | 0 | 0 | - | - | 29.9 | 49.5 | 0 | 0 | 0 | 0 | 29.4 | 30.2 | 28.8 | 1.52 | 4.9 | 4.1 | 0 | 28.7 | 29.6 | 28.2 | 1.53 | 4.1 | 3.8 | 25.2 | 25.1 | 27.5 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 18:55:00 | 3948.76 | 1913.5 | 762590.04 | 732589.26 | 51.81 | 2317.37 | 2110.728 | -1257.248 | 50 | 170 | 27 | 56.1 | 27.7 | 55.2 | 0 | 0 | - | - | 29.8 | 49.6 | 0 | 0 | 0 | 0 | 29.3 | 30.2 | 28.8 | 1.52 | 4.9 | 4 | 0 | 28.7 | 29.6 | 28.3 | 1.53 | 4.1 | 3.8 | 25.2 | 25.1 | 27.4 | 1.56 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:00:00 | 3948.76 | 2027.4 | 762590.04 | 732707.88 | 51.97 | 2450.214 | 1977.882 | -1462.333 | 47 | 170 | 27 | 56.1 | 27.7 | 55.1 | 0 | 0 | - | - | 29.8 | 49.7 | 0 | 0 | 0 | 0 | 29.3 | 30.2 | 28.8 | 1.52 | 4.9 | 3.9 | 0 | 28.7 | 29.6 | 28.3 | 1.53 | 4.1 | 3.7 | 25.3 | 25.1 | 27.3 | 1.56 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:05:00 | 3948.76 | 2149.56 | 762590.04 | 732827.76 | 52.14 | 2568.3 | 1859.802 | -1451.413 | 44 | 170 | 27.1 | 56 | 27.8 | 55 | 0 | 0 | - | - | 29.8 | 49.7 | 0 | 0 | 0 | 0 | 29.1 | 30.1 | 28.7 | 1.52 | 4.8 | 3.7 | 0 | 28.6 | 29.4 | 28.3 | 1.53 | 4 | 3.5 | 25.4 | 25.2 | 27.2 | 1.56 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:10:00 | 3948.76 | 2272.08 | 762590.04 | 732948.04 | 52.32 | 2693.76 | 1734.336 | -1458.568 | 41 | 170 | 27.2 | 56 | 27.9 | 54.9 | 0 | 0 | - | - | 29.8 | 49.7 | 0 | 0 | 0 | 0 | 28.8 | 29.9 | 28.4 | 1.52 | 4.6 | 3.4 | 0 | 28.3 | 29.3 | 28.3 | 1.53 | 3.8 | 3.3 | 25.5 | 25.3 | 27.1 | 1.56 | 1.56 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:15:00 | 3948.76 | 2393.66 | 762590.04 | 733070.38 | 52.51 | 2826.604 | 1601.496 | -1452.052 | 39 | 170 | 27.3 | 56 | 27.9 | 55.2 | 0 | 0 | - | - | 29.8 | 49.8 | 0 | 0 | 0 | 0 | 28.7 | 29.7 | 28.2 | 1.53 | 4.3 | 3.1 | 0 | 28.3 | 29.2 | 28.2 | 1.53 | 3.6 | 3.2 | 25.7 | 25.5 | 27.1 | 1.57 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:20:00 | 3948.76 | 2525.02 | 762590.04 | 733202.92 | 52.73 | 2966.826 | 1461.27 | -1664.135 | 35 | 170 | 27.4 | 55.9 | 27.8 | 55.4 | 0 | 0 | - | - | 29.8 | 49.9 | 0 | 0 | 0 | 0 | 28.4 | 29.6 | 28.2 | 1.53 | 4.1 | 2.8 | 0 | 28.2 | 29.1 | 28.2 | 1.54 | 3.4 | 2.9 | 25.9 | 25.7 | 27.1 | 1.57 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:25:00 | 3948.76 | 2660.94 | 762590.04 | 733338.94 | 52.95 | 3107.052 | 1321.05 | -1663.897 | 32 | 170 | 27.5 | 55.8 | 28.2 | 54.9 | 0 | 0 | - | - | 29.8 | 50 | 0 | 0 | 0 | 0 | 28.3 | 29.4 | 28.1 | 1.53 | 3.8 | 2.6 | 0 | 28.1 | 28.8 | 28.2 | 1.54 | 3.1 | 2.8 | 26.2 | 25.9 | 27.1 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:30:00 | 3948.76 | 2802.02 | 762590.04 | 733477.36 | 53.21 | 3254.652 | 1173.444 | -1657.693 | 29 | 170 | 27.7 | 55.8 | 28.6 | 54.4 | 0 | 0 | - | - | 29.8 | 50 | 0 | 0 | 0 | 0 | 28.3 | 29.2 | 28 | 1.54 | 3.4 | 2.5 | 0 | 27.9 | 28.7 | 28.1 | 1.54 | 2.8 | 2.5 | 26.6 | 26.4 | 27.2 | 1.58 | 1.59 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:35:00 | 3948.76 | 2938.76 | 762590.04 | 733617.52 | 53.54 | 3409.638 | 1018.458 | -1667.822 | 25 | 170 | 27.8 | 55.7 | 28.9 | 54.1 | 0 | 0 | - | - | 29.8 | 50.1 | 0 | 0 | 0 | 0 | 28.2 | 29.1 | 27.9 | 1.54 | 3 | 2.3 | 0 | 27.9 | 28.6 | 28.1 | 1.55 | 2.4 | 2.5 | 25.6 | 26.7 | 27.2 | 2.57 | 1.04 | 2.62 | 1.07 | 203 | 182 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:40:00 | 3948.76 | 3077.46 | 762590.04 | 733755.4 | 54.21 | 3542.478 | 885.618 | -1660.193 | 22 | 170 | 27.8 | 55.7 | 29.1 | 53.8 | 0 | 0 | - | - | 29.8 | 50.2 | 219 | 183 | 57.1 | 57.7 | 60.6 | 26.4 | 42.3 | 2.52 | 12.7 | 15.6 | 0 | 61.5 | 26.2 | 43.5 | 2.67 | 11.3 | 14.8 | 22.6 | 24.4 | 27.9 | 2.4 | 1.09 | 2.52 | 1.09 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:45:00 | 3948.76 | 3215.24 | 762590.04 | 733891.42 | 54.88 | 3719.604 | 708.492 | -1630.611 | 18 | 170 | 27.6 | 56 | 29.2 | 53.7 | 0 | 0 | - | - | 29.8 | 50.2 | 224 | 183 | 51.1 | 50.9 | 66.2 | 24.3 | 40.4 | 2.32 | 11.3 | 24.5 | 50.8 | 69.1 | 24.2 | 42.6 | 2.48 | 11.2 | 25.4 | 22 | 23.8 | 28.2 | 2.42 | 1.07 | 2.53 | 1.07 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:50:00 | 3948.76 | 3336.42 | 762590.04 | 734014.32 | 55.54 | 3889.35 | 538.752 | -1333.127 | 14 | 170 | 27.6 | 56.1 | 29.2 | 53.7 | 0 | 0 | - | - | 29.9 | 50.2 | 224 | 183 | 51.6 | 51.9 | 67 | 23.8 | 40.4 | 2.31 | 11.1 | 25.3 | 51.9 | 70 | 23.8 | 42.7 | 2.49 | 10.9 | 26.1 | 21.9 | 23.7 | 27.9 | 2.4 | 1.07 | 2.52 | 1.08 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 19:55:00 | 3948.76 | 3432.76 | 762590.04 | 734110.22 | 56.21 | 3985.29 | 442.806 | -1130.974 | 11 | 170 | 27.8 | 55.9 | 29.3 | 53.5 | 0 | 0 | - | - | 29.9 | 50.2 | 224 | 183 | 51.6 | 51.9 | 66.6 | 23.8 | 40 | 2.29 | 11.1 | 25.3 | 51.9 | 70 | 23.8 | 42.7 | 2.48 | 10.9 | 26.2 | 22 | 23.8 | 28.6 | 2.37 | 1.07 | 2.52 | 1.08 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:00:00 | 3948.76 | 3513.46 | 762590.04 | 734188.76 | 56.88 | 4029.57 | 398.526 | -938.016 | 10 | 170 | 27.8 | 55.8 | 29.3 | 53.6 | 0 | 0 | - | - | 30 | 50.2 | 224 | 183 | 51.6 | 51.4 | 66.2 | 23.9 | 39.7 | 2.29 | 11.2 | 24.9 | 51.4 | 69.8 | 23.8 | 42.6 | 2.47 | 10.9 | 26.2 | 22 | 23.8 | 28.1 | 2.38 | 1.07 | 2.52 | 1.08 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:05:00 | 3948.76 | 3590.08 | 762590.04 | 734266.04 | 57.54 | 4118.136 | 309.966 | -952.24 | 8 | 170 | 27.9 | 55.8 | 29.3 | 53.5 | 0 | 0 | - | - | 30 | 50.2 | 224 | 183 | 51.7 | 51.4 | 66.6 | 23.9 | 40.1 | 2.31 | 11.1 | 25.1 | 51.9 | 70 | 23.9 | 42.7 | 2.48 | 10.9 | 26.2 | 22 | 23.8 | 28.1 | 2.41 | 1.07 | 2.53 | 1.08 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:10:00 | 3948.76 | 3649.44 | 762590.04 | 734324.32 | 58.21 | 4162.416 | 265.686 | -428.762 | 7 | 170 | 28 | 55.7 | 29.2 | 53.7 | 0 | 0 | - | - | 30 | 50.3 | 224 | 183 | 52 | 52 | 66.8 | 23.9 | 40.2 | 2.31 | 11.2 | 25.2 | 51.9 | 70.1 | 23.8 | 42.7 | 2.49 | 10.9 | 26.2 | 22 | 23.8 | 28.3 | 2.38 | 1.07 | 2.52 | 1.08 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:15:00 | 3948.76 | 3681.78 | 762590.04 | 734356.92 | 58.88 | 4162.416 | 265.686 | -232.477 | 7 | 170 | 28 | 55.6 | 29.1 | 53.8 | 0 | 0 | - | - | 30 | 50.3 | 224 | 183 | 51.4 | 51.5 | 66.3 | 23.9 | 39.9 | 2.31 | 11.2 | 24.7 | 51.4 | 69.9 | 23.8 | 42.6 | 2.47 | 10.9 | 26.2 | 22 | 23.8 | 27.9 | 2.43 | 1.07 | 2.54 | 1.08 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:20:00 | 3948.76 | 3700.2 | 762590.04 | 734374.82 | 59.54 | 4177.176 | 250.924 | -239.849 | 6 | 170 | 28 | 55.6 | 29 | 54.1 | 0 | 0 | - | - | 30 | 50.4 | 224 | 183 | 52 | 52.4 | 67.1 | 23.8 | 40.6 | 2.32 | 11.1 | 25.4 | 52.4 | 70.3 | 23.8 | 42.9 | 2.5 | 10.9 | 26.3 | 21.9 | 23.7 | 27.8 | 2.4 | 1.06 | 2.54 | 1.07 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:25:00 | 3948.76 | 3718.3 | 762590.04 | 734393.1 | 60.2 | 4206.697 | 221.4 | -219.746 | 6 | 170 | 27.9 | 55.6 | 28.9 | 54.2 | 0 | 0 | - | - | 30 | 50.5 | 224 | 183 | 52.1 | 52 | 67 | 23.7 | 40.3 | 2.32 | 11 | 25.1 | 51.9 | 70.2 | 23.7 | 42.9 | 2.49 | 10.7 | 26.3 | 21.7 | 23.6 | 27.6 | 2.4 | 1.07 | 2.52 | 1.07 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:30:00 | 3948.76 | 3736.76 | 762590.04 | 734411.4 | 60.85 | 4206.697 | 221.4 | -214.714 | 6 | 170 | 27.9 | 55.6 | 28.7 | 54.3 | 0 | 0 | - | - | 30 | 50.5 | 224 | 183 | 52 | 51.8 | 66.9 | 23.6 | 40.5 | 2.35 | 11 | 24.7 | 51.9 | 69.9 | 23.6 | 42.6 | 2.48 | 10.8 | 26.2 | 21.6 | 23.4 | 27.6 | 2.39 | 1.06 | 2.52 | 1.07 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:35:00 | 3948.76 | 3755.32 | 762590.04 | 734429.86 | 61.51 | 4206.697 | 221.4 | -11.185 | 5 | 170 | 27.9 | 55.6 | 28.6 | 54.6 | 0 | 0 | - | - | 30 | 50.5 | 224 | 183 | 52 | 52 | 66.7 | 23.4 | 40.2 | 2.31 | 11 | 25.1 | 51.9 | 69.9 | 23.4 | 42.6 | 2.48 | 10.7 | 26.2 | 21.4 | 23.2 | 27.6 | 2.36 | 1.05 | 2.53 | 1.06 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:40:00 | 3948.76 | 3756.12 | 762590.04 | 734430.58 | 62.15 | 4206.697 | 221.4 | -6.149 | 5 | 170 | 27.9 | 55.5 | 28.4 | 54.8 | 0 | 0 | - | - | 30 | 50.6 | 224 | 183 | 52 | 51.8 | 66.3 | 23.2 | 39.6 | 2.28 | 11 | 25.2 | 52.4 | 70.2 | 23.2 | 42.7 | 2.48 | 10.8 | 26.5 | 21.2 | 23.1 | 27.2 | 2.34 | 1.05 | 2.51 | 1.06 | 224 | 183 | 2400 | 2400
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:45:00 | 3948.76 | 3756.8 | 762590.04 | 734431.22 | 62.8 | 4206.697 | 221.4 | -9.126 | 5 | 170 | 27.8 | 55.5 | 28.2 | 55 | 0 | 0 | - | - | 30 | 50.6 | 224 | 183 | 51.7 | 51.8 | 65.9 | 23.1 | 39.4 | 2.26 | 11 | 25.1 | 51.9 | 70 | 23.1 | 42.6 | 2.47 | 10.7 | 26.3 | 21.1 | 22.8 | 27.3 | 2.35 | 1.04 | 2.52 | 1.05 | 224 | 183 | 2404 | 2404
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:50:00 | 3948.76 | 3757.64 | 762590.04 | 734432.06 | 63.47 | 4206.697 | 221.4 | 10.577 | 5 | 170 | 27.8 | 55.4 | 28.1 | 55.1 | 0 | 0 | - | - | 30 | 50.6 | 224 | 183 | 52.2 | 52 | 66.1 | 22.9 | 39.4 | 2.28 | 11.2 | 25 | 51.9 | 70.1 | 22.8 | 42.6 | 2.48 | 10.8 | 26.4 | 20.8 | 22.6 | 27.4 | 2.37 | 1.03 | 2.53 | 1.04 | 224 | 183 | 2517 | 2517
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 20:55:00 | 3948.8 | 3758.24 | 762590.08 | 734432.66 | 64.15 | 4206.697 | 221.4 | -8.445 | 5 | 170 | 27.7 | 55.4 | 27.9 | 55.1 | 0 | 0 | - | - | 29.9 | 50.7 | 224 | 183 | 52.8 | 53.3 | 66.8 | 22.7 | 39.7 | 2.29 | 11.2 | 25.5 | 53.4 | 70.6 | 22.6 | 42.8 | 2.49 | 10.7 | 26.7 | 20.4 | 22.3 | 27.2 | 2.37 | 1.03 | 2.52 | 1.03 | 224 | 183 | 2518 | 2518
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:00:00 | 3948.8 | 3758.64 | 762590.08 | 734433.08 | 64.84 | 4206.697 | 221.4 | -9.987 | 5 | 170 | 27.7 | 55.4 | 27.8 | 55.2 | 0 | 0 | - | - | 29.9 | 50.7 | 224 | 183 | 52.9 | 53.6 | 66.7 | 22.3 | 39.7 | 2.28 | 11 | 25.6 | 52.8 | 70.5 | 22.2 | 42.6 | 2.49 | 10.6 | 26.7 | 20.2 | 22.1 | 27.5 | 2.35 | 1.02 | 2.52 | 1.03 | 224 | 183 | 2518 | 2518
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:05:00 | 3949.88 | 3758.8 | 762591.24 | 734433.22 | 65.52 | 4206.697 | 221.4 | 48.856 | 5 | 170 | 27.6 | 55.3 | 27.7 | 55.2 | 0 | 0 | - | - | 29.9 | 50.6 | 224 | 183 | 52.8 | 53.1 | 66.7 | 22.2 | 39.6 | 2.29 | 11 | 25.5 | 52.8 | 70.5 | 22.1 | 42.6 | 2.48 | 10.6 | 26.8 | 19.9 | 21.8 | 28.3 | 2.36 | 1.01 | 2.5 | 1.02 | 224 | 183 | 2518 | 2518
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:10:00 | 3955 | 3758.8 | 762596.4 | 734433.22 | 66.2 | 4206.697 | 221.4 | 43.18 | 6 | 170 | 27.5 | 55.3 | 27.6 | 55.3 | 0 | 0 | - | - | 29.9 | 50.7 | 224 | 183 | 52.3 | 52.5 | 66.6 | 21.9 | 39.4 | 2.27 | 10.9 | 25.7 | 52.3 | 70.4 | 21.8 | 42.4 | 2.46 | 10.5 | 26.9 | 19.7 | 21.6 | 27.8 | 2.37 | 1.01 | 2.5 | 1.01 | 224 | 183 | 2518 | 2518
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:15:00 | 3955.72 | 3759.6 | 762597 | 734434.02 | 66.87 | 4177.176 | 250.924 | -10 | 6 | 170 | 27.4 | 55.2 | 27.5 | 55.2 | 0 | 0 | - | - | 29.9 | 50.7 | 224 | 183 | 52.9 | 52.7 | 66.9 | 21.7 | 39.8 | 2.3 | 10.9 | 25.5 | 52.8 | 70.4 | 21.6 | 42.4 | 2.47 | 10.5 | 26.8 | 19.6 | 21.3 | 27.7 | 2.37 | 1 | 2.51 | 1.01 | 224 | 183 | 2521 | 2521
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:20:00 | 3955.72 | 3760.72 | 762597 | 734435.14 | 67.56 | 4206.697 | 221.4 | 4.635 | 5 | 170 | 27.3 | 55.2 | 27.4 | 55.3 | 0 | 0 | - | - | 29.8 | 50.6 | 224 | 183 | 52.9 | 53.1 | 67.1 | 21.4 | 39.7 | 2.29 | 10.9 | 25.9 | 52.8 | 70.5 | 21.3 | 42.4 | 2.47 | 10.5 | 27 | 19.3 | 21.2 | 27.7 | 2.37 | 0.99 | 2.51 | 1 | 224 | 183 | 2529 | 2529
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:25:00 | 3955.74 | 3761.82 | 762597.02 | 734436.3 | 68.26 | 4206.697 | 221.4 | -13.539 | 5 | 170 | 27.2 | 55.2 | 27.2 | 55.3 | 0 | 0 | - | - | 29.8 | 50.6 | 224 | 183 | 53.8 | 53.5 | 67.2 | 21.2 | 39.7 | 2.29 | 10.9 | 25.9 | 53.3 | 70.8 | 21.2 | 42.5 | 2.48 | 10.6 | 27.2 | 19.2 | 20.9 | 27.9 | 2.37 | 0.98 | 2.52 | 0.99 | 224 | 183 | 2559 | 2559
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:30:00 | 3955.8 | 3762.72 | 762597.08 | 734437.18 | 68.99 | 4199.316 | 228.781 | -11.497 | 5 | 170 | 27.1 | 55.1 | 27.1 | 55.2 | 0 | 0 | - | - | 29.8 | 50.5 | 224 | 183 | 53.7 | 53.4 | 67.5 | 21.1 | 39.7 | 2.29 | 11 | 26.3 | 53.8 | 71.1 | 20.9 | 42.6 | 2.47 | 10.7 | 27.5 | 18.8 | 20.7 | 27.7 | 2.37 | 0.98 | 2.52 | 0.99 | 224 | 183 | 2610 | 2610
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:35:00 | 3955.8 | 3763.74 | 762597.08 | 734438.16 | 69.72 | 4199.316 | 228.781 | -11.119 | 5 | 170 | 27 | 55 | 27 | 55.3 | 0 | 0 | - | - | 29.8 | 50.5 | 224 | 183 | 54.4 | 54.4 | 67.7 | 20.7 | 40 | 2.31 | 10.9 | 26.2 | 54.5 | 71.3 | 20.7 | 42.6 | 2.48 | 10.5 | 27.6 | 18.6 | 20.3 | 27.8 | 2.38 | 0.97 | 2.51 | 0.98 | 224 | 183 | 2652 | 2652
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:40:00 | 3955.82 | 3764.78 | 762597.1 | 734439.2 | 70.43 | 4206.697 | 221.4 | -11.385 | 5 | 170 | 26.9 | 54.9 | 26.9 | 55.2 | 0 | 0 | - | - | 29.8 | 50.4 | 224 | 183 | 53.9 | 53.9 | 68 | 20.5 | 39.9 | 2.29 | 10.8 | 26.7 | 54 | 71.2 | 20.3 | 42.4 | 2.47 | 10.5 | 27.7 | 18.3 | 20.1 | 28.2 | 2.36 | 0.96 | 2.51 | 0.97 | 224 | 183 | 2667 | 2667
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:45:00 | 3955.82 | 3765.82 | 762597.1 | 734440.24 | 71.16 | 4206.697 | 221.4 | -13.364 | 5 | 170 | 26.9 | 54.9 | 26.7 | 55.2 | 0 | 0 | - | - | 29.8 | 50.3 | 224 | 183 | 54.4 | 54 | 67.6 | 20.2 | 39.6 | 2.28 | 10.8 | 26.5 | 54 | 71.3 | 20.1 | 42.4 | 2.47 | 10.4 | 27.8 | 18.1 | 19.8 | 28.8 | 2.36 | 0.96 | 2.51 | 0.96 | 224 | 183 | 2682 | 2682
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:50:00 | 3955.82 | 3766.86 | 762597.1 | 734441.32 | 71.89 | 4214.076 | 214.02 | -17.018 | 5 | 170 | 26.7 | 54.9 | 26.5 | 55.2 | 0 | 0 | - | - | 29.7 | 50.2 | 224 | 183 | 53.7 | 54 | 67.7 | 19.9 | 39.5 | 2.27 | 10.8 | 26.7 | 54 | 71.2 | 19.8 | 42.4 | 2.46 | 10.4 | 27.8 | 17.7 | 19.6 | 28.9 | 2.36 | 0.95 | 2.5 | 0.96 | 224 | 183 | 2704 | 2704
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 21:55:00 | 3955.84 | 3767.8 | 762597.12 | 734442.24 | 72.6 | 4206.697 | 221.4 | -13.507 | 5 | 170 | 26.5 | 54.8 | 26.4 | 55.2 | 0 | 0 | - | - | 29.7 | 50.2 | 224 | 183 | 53.8 | 54 | 68 | 19.7 | 39.4 | 2.26 | 10.8 | 27.1 | 54 | 71.2 | 19.6 | 42.2 | 2.45 | 10.4 | 28 | 17.6 | 19.3 | 28.1 | 2.36 | 0.94 | 2.51 | 0.95 | 224 | 183 | 2727 | 2754
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:00:00 | 3955.84 | 3768.84 | 762597.12 | 734443.26 | 73.34 | 4206.697 | 221.4 | -13.442 | 5 | 170 | 26.5 | 54.6 | 26.3 | 55.2 | 0 | 0 | - | - | 29.7 | 50.1 | 224 | 183 | 54.3 | 54 | 68 | 19.4 | 39.4 | 2.26 | 10.8 | 27.2 | 54.5 | 71.4 | 19.3 | 42.4 | 2.46 | 10.5 | 28.1 | 17.2 | 19.2 | 28.2 | 2.33 | 0.93 | 2.48 | 0.94 | 224 | 183 | 2740 | 2740
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:05:00 | 3955.84 | 3769.9 | 762597.12 | 734444.32 | 73.56 | 4221.457 | 206.64 | -14.69 | 5 | 170 | 26.5 | 54.7 | 26.2 | 55.4 | 0 | 0 | - | - | 29.6 | 50.1 | 0 | 0 | 45.5 | 46 | 66.9 | 19.3 | 38.3 | 2.12 | 10.5 | 29.2 | 46.1 | 70.6 | 19.2 | 41.6 | 2.3 | 10.9 | 30.2 | 21.1 | 20.9 | 27.7 | 1.55 | 1.37 | 1.59 | 1.38 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:10:00 | 3955.84 | 3770.98 | 762597.12 | 734445.44 | 73.67 | 4228.837 | 199.26 | -12.062 | 5 | 170 | 26.4 | 55.1 | 26.1 | 55.7 | 0 | 0 | - | - | 29.6 | 50 | 0 | 0 | 0 | 0 | 36.7 | 31.5 | 29.9 | 1.47 | 10.1 | 12.5 | 0 | 34.1 | 34.6 | 30.2 | 1.52 | 13 | 9.4 | 22.4 | 22.2 | 26.8 | 1.44 | 1.43 | 1.43 | 1.44 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:15:00 | 3955.88 | 3772 | 762597.16 | 734446.44 | 73.77 | 4228.837 | 199.26 | -13.194 | 5 | 170 | 26.2 | 55.4 | 26.1 | 55.9 | 0 | 0 | - | - | 29.5 | 50 | 0 | 0 | 0 | 0 | 29.7 | 36.1 | 28.8 | 1.41 | 13.6 | 7 | 0 | 28.4 | 40.2 | 28.6 | 1.42 | 17.5 | 6 | 22.9 | 22.7 | 26.4 | 1.45 | 1.45 | 1.45 | 1.46 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:20:00 | 3955.9 | 3772.96 | 762597.18 | 734447.4 | 73.87 | 4206.697 | 221.4 | -13.388 | 5 | 170 | 26.2 | 55.6 | 26 | 56.1 | 0 | 0 | - | - | 29.5 | 49.9 | 0 | 0 | 0 | 0 | 29.3 | 34.9 | 28.6 | 1.43 | 12 | 6.2 | 0 | 28.6 | 38.7 | 28.4 | 1.44 | 15.5 | 5.8 | 23.2 | 23 | 26.6 | 1.47 | 1.46 | 1.45 | 1.47 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:25:00 | 3955.9 | 3773.94 | 762597.18 | 734448.36 | 73.96 | 4206.697 | 221.4 | -12.796 | 5 | 170 | 26.1 | 55.7 | 25.9 | 56.1 | 0 | 0 | - | - | 29.4 | 50 | 0 | 0 | 0 | 0 | 29.2 | 34.1 | 28.4 | 1.44 | 10.9 | 6 | 0 | 28.9 | 37.1 | 28.2 | 1.44 | 13.6 | 5.9 | 23.3 | 23.1 | 26.7 | 1.47 | 1.47 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:30:00 | 3955.9 | 3774.92 | 762597.18 | 734449.34 | 74.05 | 4206.697 | 221.4 | -9.336 | 5 | 170 | 26 | 55.8 | 25.9 | 56.3 | 0 | 0 | - | - | 29.4 | 50 | 0 | 0 | 0 | 0 | 29.1 | 33.4 | 28.2 | 1.44 | 10.1 | 5.6 | 0 | 28.9 | 35.7 | 27.9 | 1.45 | 12.2 | 5.8 | 23.4 | 23.2 | 26.7 | 1.48 | 1.47 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:35:00 | 3955.94 | 3776 | 762597.22 | 734450.44 | 74.13 | 4243.596 | 184.5 | -14.284 | 5 | 170 | 26 | 55.9 | 25.9 | 56.4 | 0 | 0 | - | - | 29.3 | 50 | 0 | 0 | 0 | 0 | 28.8 | 33.1 | 27.9 | 1.44 | 9.6 | 5.3 | 0 | 28.8 | 34.7 | 27.8 | 1.45 | 11.1 | 5.6 | 23.5 | 23.3 | 27.1 | 1.48 | 1.47 | 1.47 | 1.48 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:40:00 | 3955.96 | 3776.84 | 762597.24 | 734451.28 | 74.21 | 4206.697 | 221.4 | -12.79 | 5 | 170 | 25.9 | 56 | 25.8 | 56.4 | 0 | 0 | - | - | 29.2 | 50.1 | 0 | 0 | 0 | 0 | 28.7 | 32.6 | 27.8 | 1.45 | 9.2 | 5.2 | 0 | 28.7 | 34.1 | 27.7 | 1.45 | 10.4 | 5.5 | 23.5 | 23.3 | 27.3 | 1.48 | 1.47 | 1.47 | 1.48 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:45:00 | 3955.96 | 3777.9 | 762597.24 | 734452.34 | 74.3 | 4250.976 | 177.12 | -11.98 | 5 | 170 | 25.9 | 56.1 | 25.8 | 56.5 | 0 | 0 | - | - | 29.2 | 50.1 | 0 | 0 | 0 | 0 | 28.6 | 32.4 | 27.8 | 1.45 | 8.9 | 5 | 0 | 28.7 | 33.6 | 27.7 | 1.45 | 9.9 | 5.3 | 23.5 | 23.4 | 27.3 | 1.48 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:50:00 | 3956.02 | 3778.56 | 762597.3 | 734453 | 74.38 | 4206.697 | 221.4 | -12.171 | 5 | 170 | 25.8 | 56.2 | 25.7 | 56.6 | 0 | 0 | - | - | 29.2 | 50.2 | 0 | 0 | 0 | 0 | 28.6 | 32.9 | 27.9 | 1.45 | 9.3 | 4.8 | 0 | 28.6 | 33.6 | 27.6 | 1.46 | 9.8 | 5.2 | 23.6 | 23.3 | 27.3 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 22:55:00 | 3956.02 | 3779.5 | 762597.3 | 734453.92 | 74.45 | 4250.976 | 177.12 | -12.221 | 5 | 170 | 25.8 | 56.3 | 25.7 | 56.6 | 0 | 0 | - | - | 29.1 | 50.1 | 0 | 0 | 0 | 0 | 28.2 | 34.1 | 28.1 | 1.45 | 10.5 | 4.5 | 0 | 28.6 | 33.5 | 27.6 | 1.46 | 9.7 | 5.2 | 23.6 | 23.4 | 27.2 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:00:00 | 3956.04 | 3780.28 | 762597.32 | 734454.72 | 74.53 | 4250.976 | 177.12 | -7.076 | 5 | 170 | 25.8 | 56.3 | 25.7 | 56.7 | 0 | 0 | - | - | 29.1 | 50.1 | 0 | 0 | 0 | 0 | 28.1 | 35 | 28.2 | 1.45 | 11.5 | 4.3 | 0 | 28.6 | 33.4 | 27.6 | 1.46 | 9.5 | 5.2 | 23.6 | 23.4 | 27.2 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:05:00 | 3956.04 | 3784.82 | 762597.32 | 734459.28 | 74.6 | 4250.976 | 177.12 | -9.411 | 5 | 170 | 25.7 | 56.4 | 25.7 | 56.7 | 0 | 0 | - | - | 29.1 | 50.1 | 0 | 0 | 0 | 0 | 27.9 | 35.1 | 28.2 | 1.45 | 11.4 | 4.2 | 0 | 28.4 | 33.1 | 27.6 | 1.46 | 9.3 | 5.1 | 23.6 | 23.4 | 27.2 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:10:00 | 3956.14 | 3785.58 | 762597.42 | 734460.02 | 74.68 | 4250.976 | 177.12 | -12.975 | 5 | 170 | 25.7 | 56.4 | 25.6 | 56.7 | 0 | 0 | - | - | 29 | 50.2 | 0 | 0 | 0 | 0 | 27.9 | 34.4 | 28.1 | 1.45 | 10.8 | 4.2 | 0 | 28.3 | 32.6 | 27.6 | 1.46 | 8.8 | 4.9 | 23.6 | 23.4 | 26.9 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:15:00 | 3956.14 | 3786.36 | 762597.42 | 734460.82 | 74.76 | 4250.976 | 177.12 | -13.094 | 5 | 170 | 25.7 | 56.4 | 25.6 | 56.7 | 0 | 0 | - | - | 29 | 50.1 | 0 | 0 | 0 | 0 | 27.9 | 33.7 | 27.9 | 1.45 | 10 | 4.1 | 0 | 28.2 | 32.2 | 27.6 | 1.46 | 8.4 | 4.7 | 23.6 | 23.4 | 26.9 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:20:00 | 3956.18 | 3787.18 | 762597.46 | 734461.6 | 74.83 | 4250.976 | 177.12 | 5.341 | 5 | 170 | 25.7 | 56.5 | 25.6 | 56.8 | 0 | 0 | - | - | 29 | 50.2 | 0 | 0 | 0 | 0 | 27.9 | 33.1 | 27.7 | 1.45 | 9.4 | 4.1 | 0 | 28.1 | 31.8 | 27.4 | 1.46 | 8 | 4.6 | 23.7 | 23.5 | 27.1 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:25:00 | 3956.22 | 3787.96 | 762597.5 | 734462.4 | 74.9 | 4250.976 | 177.12 | -42.209 | 5 | 170 | 25.6 | 56.5 | 25.5 | 56.9 | 0 | 0 | - | - | 29 | 50.2 | 0 | 0 | 0 | 0 | 27.9 | 32.6 | 27.7 | 1.45 | 8.8 | 4.1 | 0 | 27.9 | 31.4 | 27.4 | 1.46 | 7.6 | 4.5 | 23.7 | 23.5 | 26.9 | 1.49 | 1.48 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:30:00 | 3956.26 | 3788.72 | 762597.54 | 734463.18 | 74.97 | 4250.976 | 177.12 | -24.41 | 5 | 170 | 25.6 | 56.6 | 25.4 | 57 | 0 | 0 | - | - | 29 | 50.2 | 0 | 0 | 0 | 0 | 27.9 | 32.1 | 27.6 | 1.45 | 8.4 | 4.1 | 0 | 27.9 | 31.1 | 27.4 | 1.46 | 7.2 | 4.5 | 23.7 | 23.5 | 27 | 1.49 | 1.49 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:35:00 | 3956.34 | 3789.58 | 762597.62 | 734464 | 75.05 | 4228.836 | 199.26 | -10.215 | 5 | 170 | 25.6 | 56.6 | 25.5 | 57 | 0 | 0 | - | - | 28.9 | 50.2 | 0 | 0 | 0 | 0 | 27.9 | 31.8 | 27.6 | 1.46 | 8.1 | 4.1 | 0 | 27.9 | 30.8 | 27.4 | 1.46 | 6.9 | 4.5 | 23.7 | 23.5 | 27.2 | 1.49 | 1.49 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:40:00 | 3956.34 | 3790.34 | 762597.62 | 734464.76 | 75.12 | 4243.596 | 184.5 | -9.824 | 5 | 170 | 25.5 | 56.7 | 25.5 | 56.9 | 0 | 0 | - | - | 28.9 | 50.2 | 0 | 0 | 0 | 0 | 28 | 31.7 | 27.7 | 1.45 | 7.9 | 4.2 | 0 | 27.9 | 30.6 | 27.4 | 1.46 | 6.6 | 4.5 | 23.7 | 23.5 | 27.3 | 1.49 | 1.49 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:45:00 | 3956.34 | 3791.08 | 762597.62 | 734465.52 | 75.19 | 4250.976 | 177.12 | -10.009 | 5 | 170 | 25.5 | 56.6 | 25.5 | 56.9 | 0 | 0 | - | - | 28.9 | 50.2 | 0 | 0 | 0 | 0 | 28.1 | 31.6 | 27.7 | 1.46 | 7.8 | 4.3 | 0 | 27.9 | 30.3 | 27.5 | 1.46 | 6.4 | 4.5 | 23.7 | 23.5 | 27.3 | 1.49 | 1.49 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:50:00 | 3956.4 | 3792.04 | 762597.68 | 734466.46 | 75.26 | 4250.976 | 177.12 | -1.185 | 5 | 170 | 25.5 | 56.7 | 25.5 | 56.9 | 0 | 0 | - | - | 28.9 | 50.2 | 0 | 0 | 0 | 0 | 28.2 | 31.4 | 27.7 | 1.46 | 7.7 | 4.3 | 0 | 27.9 | 30.2 | 27.5 | 1.46 | 6.2 | 4.4 | 23.7 | 23.5 | 27.1 | 1.49 | 1.49 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B22-SmartLogger/B22-ESS04 | 2026-06-02 23:55:00 | 3956.44 | 3792.78 | 762597.72 | 734467.2 | 75.33 | 4250.976 | 177.12 | -7.388 | 5 | 170 | 25.5 | 56.7 | 25.5 | 56.9 | 0 | 0 | - | - | 28.9 | 50.3 | 0 | 0 | 0 | 0 | 28.2 | 31.2 | 27.7 | 1.46 | 7.5 | 4.3 | 0 | 27.9 | 30.1 | 27.5 | 1.46 | 6.1 | 4.5 | 23.7 | 23.5 | 26.9 | 1.49 | 1.49 | 1.48 | 1.49 | 0 | 0 | 0 | 0