## 5 minutes
Time range: | 2026-06-02 00:00:00 - 2026-06-02 23:59:59
Export time: | 2026-06-03 00:17:10
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge energy(kWh) | Total discharge energy(kWh) | Daily auxiliary power consumption(kWh) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge power(kW) | SOC(%) | Equivalent number of cycles | Battery cabin temperature 1(℃) | Battery cabin humidity 1(%) | Battery cabin temperature 2(℃) | Battery cabin humidity 2(%) | CO concentration 1(ppm) | CO concentration 2(ppm) | H2 concentration 1(ppm) | H2 concentration 2(ppm) | Control unit cabin temperature 1(℃) | Control unit cabin humidity 1(%) | Control status of EEV 1(step) | Control status of EEV 2(step) | Running status of outdoor fan 1(%) | Running status of outdoor fan 2(%) | Discharge temperature of compressor 1(℃) | Suction temperature of refrigerant system 1(℃) | Condenser outlet temperature of refrigerant system 1(℃) | Condenser outlet pressure of refrigerant system 1(Mpa) | Suction superheat degree of refrigerant system 1(℃) | Discharge superheat degree of compressor 1(℃) | Running status of outdoor fan 3(%) | Discharge temperature of compressor 2(℃) | Suction temperature of refrigerant system 2(℃) | Condenser outlet temperature of refrigerant system 2(℃) | Condenser outlet pressure of refrigerant system 2(Mpa) | Suction superheat degree of refrigerant system 2(℃) | Discharge superheat degree of compressor 2(℃) | Battery-side supply water temperature(℃) | Battery-side return water temperature(℃) | Air intake temperature(℃) | Discharge pressure of refrigerant system 1(Mpa) | Suction pressure of refrigerant system 1(Mpa) | Discharge pressure of refrigerant system 2(Mpa) | Suction pressure of refrigerant system 2(Mpa) | Running status of EEV 1(step) | Running status of EEV 2(step) | Compressor 1 running status(rpm) | Compressor 2 running status(rpm)
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:00:00 | 0 | 0 | 793793.88 | 765265.5 | 0 | 4249.188 | 223.638 | -10.62 | 5 | 177 | 26 | 56.7 | 26.1 | 57.2 | 0 | 0 | - | - | 29.8 | 51.2 | 0 | 0 | 0 | 0 | 28.6 | 30.2 | 28.3 | 1.48 | 5.7 | 4.2 | 0 | 28.3 | 30.2 | 28.5 | 1.5 | 5.6 | 4.2 | 24.4 | 24.5 | 28.1 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:05:00 | 0 | 0.82 | 793793.88 | 765266.26 | 0.08 | 4249.188 | 223.638 | -12.11 | 5 | 177 | 26 | 56.8 | 26.1 | 57.1 | 0 | 0 | - | - | 29.8 | 51.2 | 0 | 0 | 0 | 0 | 28.6 | 30.2 | 28.3 | 1.48 | 5.6 | 4.3 | 0 | 28.4 | 30.1 | 28.5 | 1.5 | 5.6 | 4.3 | 24.4 | 24.6 | 28.1 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:10:00 | 0.02 | 1.52 | 793793.9 | 765266.96 | 0.2 | 4249.188 | 223.638 | -9.481 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.8 | 51.3 | 0 | 0 | 0 | 0 | 28.6 | 30.1 | 28.3 | 1.48 | 5.4 | 4.1 | 0 | 28.3 | 30.1 | 28.5 | 1.51 | 5.5 | 4.1 | 24.4 | 24.6 | 27.7 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:15:00 | 0.02 | 2.2 | 793793.9 | 765267.64 | 0.27 | 4271.553 | 201.273 | -9.333 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.8 | 51.3 | 0 | 0 | 0 | 0 | 28.3 | 29.9 | 28.2 | 1.48 | 5.4 | 4 | 0 | 28.2 | 30.1 | 28.4 | 1.5 | 5.5 | 4.1 | 24.4 | 24.6 | 27.7 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:20:00 | 0.02 | 2.9 | 793793.9 | 765268.32 | 0.34 | 4249.188 | 223.638 | -9.486 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.7 | 51.3 | 0 | 0 | 0 | 0 | 28.2 | 29.8 | 28.2 | 1.48 | 5.2 | 3.9 | 0 | 28.2 | 29.9 | 28.4 | 1.5 | 5.4 | 4 | 24.5 | 24.6 | 27.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:25:00 | 0.12 | 3.9 | 793794 | 765269.32 | 0.41 | 4249.188 | 223.638 | -8.798 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.7 | 51.4 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 28.1 | 1.48 | 5.2 | 3.9 | 0 | 28.2 | 29.8 | 28.4 | 1.5 | 5.2 | 3.9 | 24.4 | 24.6 | 27.7 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:30:00 | 0.14 | 4.76 | 793794.02 | 765270.18 | 0.48 | 4271.553 | 201.273 | -12.733 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.7 | 51.4 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 28.1 | 1.48 | 5.1 | 3.9 | 0 | 28.1 | 29.7 | 28.4 | 1.51 | 5 | 3.9 | 24.4 | 24.6 | 27.8 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:35:00 | 0.14 | 5.56 | 793794.02 | 765271 | 0.54 | 4249.188 | 223.638 | -43.77 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.7 | 51.4 | 0 | 0 | 0 | 0 | 28.2 | 29.6 | 28.2 | 1.48 | 5 | 3.9 | 0 | 28.1 | 29.6 | 28.4 | 1.5 | 5 | 3.9 | 24.4 | 24.6 | 27.9 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:40:00 | 0.18 | 6.48 | 793794.06 | 765271.92 | 0.61 | 4249.188 | 223.638 | -9.908 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.7 | 51.4 | 0 | 0 | 0 | 0 | 28.3 | 29.6 | 28.2 | 1.48 | 4.9 | 4 | 0 | 28.1 | 29.4 | 28.4 | 1.5 | 4.8 | 3.9 | 24.4 | 24.6 | 27.8 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:45:00 | 0.22 | 7.18 | 793794.1 | 765272.62 | 0.68 | 4249.188 | 223.638 | -2.482 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.6 | 51.4 | 0 | 0 | 0 | 0 | 28.2 | 29.4 | 28.2 | 1.48 | 4.9 | 3.9 | 0 | 28.1 | 29.3 | 28.4 | 1.51 | 4.7 | 3.9 | 24.5 | 24.6 | 27.8 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:50:00 | 0.26 | 8.08 | 793794.14 | 765273.52 | 0.74 | 4271.553 | 201.273 | -10.22 | 5 | 177 | 26 | 56.9 | 26.1 | 57.2 | 0 | 0 | - | - | 29.6 | 51.5 | 0 | 0 | 0 | 0 | 28.2 | 29.3 | 28.2 | 1.48 | 4.7 | 3.9 | 0 | 28.1 | 29.2 | 28.4 | 1.5 | 4.6 | 3.9 | 24.5 | 24.7 | 27.7 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 00:55:00 | 0.28 | 8.9 | 793794.16 | 765274.34 | 0.81 | 4271.553 | 201.273 | -11.568 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.6 | 51.5 | 0 | 0 | 0 | 0 | 28.3 | 29.3 | 28.2 | 1.48 | 4.7 | 3.9 | 0 | 28.1 | 29.2 | 28.4 | 1.5 | 4.5 | 3.8 | 24.5 | 24.7 | 27.8 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:00:00 | 0.3 | 9.66 | 793794.18 | 765275.1 | 0.87 | 4271.553 | 201.273 | -11.5 | 5 | 177 | 26 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.6 | 51.5 | 0 | 0 | 0 | 0 | 28.2 | 29.2 | 28.2 | 1.48 | 4.6 | 3.9 | 0 | 28.1 | 29.1 | 28.5 | 1.5 | 4.4 | 3.9 | 24.5 | 24.7 | 27.8 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:05:00 | 0.38 | 10.46 | 793794.26 | 765275.88 | 0.94 | 4249.188 | 223.638 | -11.495 | 5 | 177 | 26 | 56.9 | 26.2 | 57.2 | 0 | 0 | - | - | 29.6 | 51.5 | 0 | 0 | 0 | 0 | 28.2 | 29.2 | 28.2 | 1.48 | 4.5 | 3.9 | 0 | 28.1 | 29 | 28.5 | 1.51 | 4.3 | 3.9 | 24.5 | 24.7 | 27.8 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:10:00 | 0.4 | 11.28 | 793794.28 | 765276.72 | 1.01 | 4264.098 | 208.728 | -11.749 | 5 | 177 | 26 | 56.8 | 26.2 | 57.2 | 0 | 0 | - | - | 29.6 | 51.6 | 0 | 0 | 0 | 0 | 28.3 | 29.1 | 28.2 | 1.48 | 4.4 | 3.9 | 0 | 28.1 | 28.9 | 28.5 | 1.51 | 4.3 | 3.9 | 24.5 | 24.7 | 27.9 | 1.52 | 1.53 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:15:00 | 0.4 | 12.24 | 793794.28 | 765277.66 | 1.07 | 4286.463 | 186.363 | -9.252 | 5 | 177 | 26 | 56.8 | 26.2 | 57.2 | 0 | 0 | - | - | 29.6 | 51.6 | 0 | 0 | 0 | 0 | 28.3 | 29.1 | 28.3 | 1.48 | 4.4 | 3.9 | 0 | 28.1 | 28.8 | 28.6 | 1.51 | 4.2 | 3.9 | 24.6 | 24.7 | 27.9 | 1.52 | 1.53 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:20:00 | 0.46 | 12.9 | 793794.34 | 765278.34 | 1.14 | 4286.463 | 186.363 | -14.39 | 5 | 177 | 26 | 56.8 | 26.2 | 57.1 | 0 | 0 | - | - | 29.5 | 51.6 | 0 | 0 | 0 | 0 | 28.4 | 29.1 | 28.3 | 1.48 | 4.4 | 3.9 | 0 | 28.2 | 28.8 | 28.6 | 1.51 | 4.2 | 3.9 | 24.6 | 24.7 | 28 | 1.52 | 1.53 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:25:00 | 0.54 | 13.9 | 793794.42 | 765279.32 | 1.2 | 4286.463 | 186.363 | -9.808 | 5 | 177 | 26 | 56.8 | 26.2 | 57.2 | 0 | 0 | - | - | 29.5 | 51.6 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.3 | 1.48 | 4.3 | 4 | 0 | 28.2 | 28.7 | 28.7 | 1.51 | 4.1 | 3.9 | 24.6 | 24.7 | 28 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:30:00 | 0.56 | 14.74 | 793794.44 | 765280.18 | 1.27 | 4286.463 | 186.363 | -7.47 | 5 | 177 | 26 | 56.8 | 26.2 | 57.1 | 0 | 0 | - | - | 29.5 | 51.6 | 0 | 0 | 0 | 0 | 28.4 | 29 | 28.4 | 1.48 | 4.3 | 4 | 0 | 28.2 | 28.7 | 28.7 | 1.51 | 4.1 | 3.9 | 24.6 | 24.7 | 28 | 1.52 | 1.53 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:35:00 | 0.64 | 15.58 | 793794.52 | 765281.02 | 1.34 | 4286.463 | 186.363 | -10.414 | 5 | 177 | 26 | 56.8 | 26.2 | 57.2 | 0 | 0 | - | - | 29.5 | 51.6 | 0 | 0 | 0 | 0 | 28.5 | 28.9 | 28.4 | 1.48 | 4.3 | 4.1 | 0 | 28.2 | 28.7 | 28.7 | 1.51 | 4 | 3.9 | 24.6 | 24.8 | 28 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:40:00 | 0.68 | 16.42 | 793794.56 | 765281.84 | 1.4 | 4256.643 | 216.183 | -10.172 | 5 | 177 | 26 | 56.8 | 26 | 57.3 | 0 | 0 | - | - | 29.5 | 51.7 | 0 | 0 | 0 | 0 | 28.5 | 28.9 | 28.4 | 1.48 | 4.3 | 4.1 | 0 | 28.2 | 28.7 | 28.7 | 1.51 | 4 | 4 | 24.6 | 24.7 | 28.1 | 1.51 | 1.53 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:45:00 | 0.7 | 17.2 | 793794.58 | 765282.64 | 1.47 | 4293.918 | 178.908 | -11.657 | 5 | 177 | 26.1 | 56.8 | 26 | 57.4 | 0 | 0 | - | - | 29.5 | 51.6 | 0 | 0 | 0 | 0 | 28.5 | 28.9 | 28.5 | 1.48 | 4.2 | 4.1 | 0 | 28.2 | 28.6 | 28.8 | 1.51 | 4 | 4 | 24.6 | 24.8 | 28.1 | 1.52 | 1.53 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:50:00 | 0.72 | 18.06 | 793794.6 | 765283.48 | 1.53 | 4264.098 | 208.728 | -9.754 | 5 | 177 | 26.1 | 56.8 | 26.1 | 57.2 | 0 | 0 | - | - | 29.5 | 51.7 | 0 | 0 | 0 | 0 | 28.5 | 28.9 | 28.5 | 1.48 | 4.3 | 4.2 | 0 | 28.2 | 28.6 | 28.7 | 1.5 | 4 | 4.1 | 24.6 | 24.8 | 28.1 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 01:55:00 | 0.78 | 18.9 | 793794.66 | 765284.34 | 1.6 | 4293.918 | 178.908 | -10.017 | 5 | 177 | 26 | 56.8 | 26.2 | 57.2 | 0 | 0 | - | - | 29.5 | 51.7 | 0 | 0 | 0 | 0 | 28.6 | 28.9 | 28.6 | 1.48 | 4.3 | 4.1 | 0 | 28.2 | 28.6 | 28.8 | 1.51 | 4 | 4.1 | 24.7 | 24.8 | 28.2 | 1.51 | 1.53 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:00:00 | 0.8 | 19.68 | 793794.68 | 765285.16 | 1.67 | 4293.918 | 178.908 | -14.505 | 5 | 177 | 26.1 | 56.9 | 26.2 | 57.1 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 28.6 | 28.9 | 28.6 | 1.48 | 4.3 | 4.2 | 0 | 28.3 | 28.6 | 28.8 | 1.5 | 4 | 4.1 | 24.7 | 24.8 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:05:00 | 0.82 | 20.6 | 793794.7 | 765286.02 | 1.73 | 4293.918 | 178.908 | -10.571 | 5 | 177 | 26 | 56.9 | 26.2 | 57.1 | 0 | 0 | - | - | 29.5 | 51.7 | 0 | 0 | 0 | 0 | 28.6 | 28.9 | 28.6 | 1.48 | 4.4 | 4.3 | 0 | 28.3 | 28.6 | 28.9 | 1.5 | 4 | 4.2 | 24.7 | 24.8 | 28.3 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:10:00 | 0.82 | 21.36 | 793794.7 | 765286.78 | 1.8 | 4256.643 | 216.183 | -10.418 | 5 | 177 | 26 | 56.9 | 26.2 | 57.1 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 28.7 | 29 | 28.7 | 1.48 | 4.4 | 4.3 | 0 | 28.3 | 28.6 | 28.9 | 1.5 | 4 | 4.1 | 24.7 | 24.8 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:15:00 | 0.9 | 22.12 | 793794.78 | 765287.54 | 1.86 | 4293.918 | 178.908 | -7.61 | 5 | 177 | 26.1 | 56.8 | 26.3 | 57.1 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 28.7 | 28.9 | 28.7 | 1.48 | 4.3 | 4.3 | 0 | 28.3 | 28.6 | 28.9 | 1.5 | 4 | 4.2 | 24.7 | 24.8 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:20:00 | 0.94 | 23 | 793794.86 | 765288.44 | 1.93 | 4293.918 | 178.908 | -8.043 | 5 | 177 | 26.1 | 56.8 | 26.1 | 57.3 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 28.7 | 29 | 28.8 | 1.48 | 4.4 | 4.4 | 0 | 28.4 | 28.6 | 29 | 1.5 | 4 | 4.2 | 24.7 | 24.9 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:25:00 | 1.02 | 23.76 | 793794.9 | 765289.18 | 1.99 | 4256.643 | 216.183 | -7.432 | 5 | 177 | 26.1 | 56.8 | 26 | 57.4 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 28.8 | 28.9 | 28.7 | 1.48 | 4.4 | 4.5 | 0 | 28.4 | 28.5 | 29 | 1.5 | 4 | 4.3 | 24.7 | 24.8 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:30:00 | 1.02 | 24.4 | 793794.9 | 765289.84 | 2.06 | 4256.643 | 216.183 | -10.892 | 5 | 177 | 26 | 56.9 | 26.2 | 57.3 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 28.7 | 28.8 | 28.7 | 1.48 | 4.3 | 4.4 | 0 | 28.4 | 28.4 | 29 | 1.5 | 3.9 | 4.2 | 24.7 | 24.9 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:35:00 | 1.02 | 25.06 | 793794.9 | 765290.5 | 2.12 | 4256.643 | 216.183 | -8.975 | 5 | 177 | 26.1 | 56.9 | 26.2 | 57.2 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 28.7 | 28.8 | 28.7 | 1.48 | 4.3 | 4.3 | 0 | 28.3 | 28.3 | 29 | 1.5 | 3.8 | 4.2 | 24.7 | 24.9 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:40:00 | 1.02 | 25.72 | 793794.9 | 765291.16 | 2.19 | 4256.643 | 216.183 | -9.009 | 5 | 177 | 26.1 | 56.9 | 26.3 | 57.1 | 0 | 0 | - | - | 29.5 | 51.9 | 0 | 0 | 0 | 0 | 28.7 | 28.7 | 28.7 | 1.48 | 4.2 | 4.4 | 0 | 28.3 | 28.3 | 29 | 1.5 | 3.8 | 4.2 | 24.7 | 24.9 | 28.2 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:45:00 | 1.02 | 26.4 | 793794.9 | 765291.82 | 2.26 | 4256.643 | 216.183 | -5.241 | 5 | 177 | 26.1 | 56.9 | 26.3 | 57.1 | 0 | 0 | - | - | 29.5 | 51.9 | 0 | 0 | 0 | 0 | 28.7 | 28.7 | 28.7 | 1.48 | 4.1 | 4.4 | 0 | 28.3 | 28.2 | 29 | 1.5 | 3.7 | 4.2 | 24.7 | 24.9 | 28.4 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:50:00 | 1.04 | 27.14 | 793794.92 | 765292.56 | 2.32 | 4256.643 | 216.183 | -9.364 | 5 | 177 | 26.1 | 56.8 | 26.3 | 57.1 | 0 | 0 | - | - | 29.5 | 51.9 | 0 | 0 | 0 | 0 | 28.7 | 28.7 | 28.7 | 1.48 | 4.1 | 4.3 | 0 | 28.3 | 28.2 | 29 | 1.5 | 3.6 | 4.2 | 24.7 | 24.9 | 28.3 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 02:55:00 | 1.04 | 27.8 | 793794.92 | 765293.24 | 2.39 | 4301.372 | 171.454 | 4.244 | 5 | 177 | 26.1 | 56.9 | 26.3 | 57.1 | 0 | 0 | - | - | 29.4 | 51.9 | 0 | 0 | 0 | 0 | 28.7 | 28.7 | 28.7 | 1.48 | 4 | 4.4 | 0 | 28.3 | 28.2 | 29 | 1.5 | 3.6 | 4.2 | 24.7 | 24.9 | 28.2 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:00:00 | 1.14 | 28.48 | 793795.02 | 765293.92 | 2.45 | 4256.643 | 216.183 | -13.17 | 5 | 177 | 26.1 | 56.9 | 26.4 | 57.1 | 0 | 0 | - | - | 29.5 | 52 | 0 | 0 | 0 | 0 | 28.7 | 28.7 | 28.7 | 1.48 | 4.1 | 4.3 | 0 | 28.4 | 28.2 | 29 | 1.5 | 3.6 | 4.2 | 24.8 | 24.9 | 28.2 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:05:00 | 1.14 | 29.08 | 793795.02 | 765294.5 | 2.52 | 4256.643 | 216.183 | -12.021 | 5 | 177 | 26.1 | 56.9 | 26.3 | 57 | 0 | 0 | - | - | 29.4 | 52 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.8 | 1.48 | 4.1 | 4.4 | 0 | 28.4 | 28.2 | 29.1 | 1.5 | 3.6 | 4.3 | 24.8 | 24.9 | 28.2 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:10:00 | 1.14 | 29.76 | 793795.02 | 765295.18 | 2.58 | 4256.643 | 216.183 | -9.374 | 5 | 177 | 26.1 | 56.9 | 26.3 | 57.1 | 0 | 0 | - | - | 29.5 | 51.9 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.8 | 1.48 | 4.1 | 4.4 | 0 | 28.4 | 28.2 | 29.1 | 1.51 | 3.6 | 4.2 | 24.8 | 24.9 | 28.3 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:15:00 | 1.14 | 30.4 | 793795.02 | 765295.82 | 2.65 | 4264.098 | 208.728 | -8.927 | 5 | 177 | 26.1 | 56.9 | 26.3 | 57 | 0 | 0 | - | - | 29.5 | 51.9 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.9 | 1.48 | 4.1 | 4.4 | 0 | 28.4 | 28.2 | 29.1 | 1.5 | 3.6 | 4.2 | 24.8 | 24.9 | 28.4 | 1.51 | 1.53 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:20:00 | 1.14 | 31.02 | 793795.02 | 765296.48 | 2.72 | 4271.553 | 201.273 | -7.375 | 5 | 177 | 26.1 | 56.9 | 26.3 | 57 | 0 | 0 | - | - | 29.5 | 51.9 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.9 | 1.48 | 4.1 | 4.4 | 0 | 28.4 | 28.2 | 29.1 | 1.51 | 3.6 | 4.2 | 24.8 | 25 | 28.4 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:25:00 | 1.16 | 31.52 | 793795.04 | 765296.94 | 2.78 | 4271.553 | 201.273 | -28.785 | 5 | 177 | 26.1 | 56.9 | 26.3 | 57 | 0 | 0 | - | - | 29.4 | 52 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.9 | 1.48 | 4.1 | 4.5 | 0 | 28.5 | 28.2 | 29.1 | 1.51 | 3.6 | 4.3 | 24.8 | 25 | 28.4 | 1.51 | 1.53 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:30:00 | 1.28 | 32.38 | 793795.16 | 765297.8 | 2.85 | 4301.372 | 171.454 | -9.437 | 5 | 177 | 26.2 | 56.9 | 26.4 | 57.1 | 0 | 0 | - | - | 29.5 | 52 | 0 | 0 | 0 | 0 | 28.9 | 28.8 | 29 | 1.48 | 4.1 | 4.5 | 0 | 28.6 | 28.2 | 29.2 | 1.51 | 3.6 | 4.3 | 24.9 | 25 | 28.3 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:35:00 | 1.28 | 33.04 | 793795.16 | 765298.48 | 2.92 | 4271.553 | 201.273 | -8.254 | 4 | 177 | 26.2 | 56.8 | 26.4 | 57.1 | 0 | 0 | - | - | 29.4 | 52 | 0 | 0 | 0 | 0 | 29.2 | 28.9 | 29.1 | 1.48 | 4.3 | 4.8 | 0 | 28.7 | 28.3 | 29.2 | 1.51 | 3.7 | 4.4 | 24.9 | 25 | 28.3 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:40:00 | 1.32 | 33.74 | 793795.2 | 765299.18 | 2.98 | 4286.463 | 186.363 | -12.404 | 4 | 177 | 26.2 | 56.9 | 26.4 | 57 | 0 | 0 | - | - | 29.5 | 52 | 0 | 0 | 0 | 0 | 29.2 | 28.9 | 29.1 | 1.48 | 4.3 | 4.7 | 0 | 28.7 | 28.3 | 29.3 | 1.51 | 3.7 | 4.4 | 24.8 | 25 | 28.3 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:45:00 | 1.32 | 34.44 | 793795.2 | 765299.88 | 3.05 | 4286.463 | 186.363 | -10.216 | 4 | 177 | 26.2 | 56.8 | 26.4 | 57 | 0 | 0 | - | - | 29.5 | 52 | 0 | 0 | 0 | 0 | 29.2 | 29 | 29.1 | 1.48 | 4.3 | 4.7 | 0 | 28.7 | 28.3 | 29.2 | 1.51 | 3.6 | 4.3 | 24.9 | 25 | 28.2 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:50:00 | 1.36 | 35.18 | 793795.24 | 765300.6 | 3.11 | 4286.463 | 186.363 | -9.154 | 4 | 177 | 26.2 | 56.8 | 26.4 | 57.1 | 0 | 0 | - | - | 29.4 | 52 | 0 | 0 | 0 | 0 | 29.3 | 29.1 | 29.2 | 1.48 | 4.4 | 4.9 | 0 | 28.7 | 28.4 | 29.3 | 1.51 | 3.7 | 4.5 | 24.9 | 25 | 27.9 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 03:55:00 | 1.36 | 35.9 | 793795.24 | 765301.34 | 3.18 | 4293.917 | 178.909 | -9.285 | 4 | 177 | 26.2 | 56.8 | 26.4 | 57 | 0 | 0 | - | - | 29.4 | 52 | 0 | 0 | 0 | 0 | 29.4 | 29.2 | 29.3 | 1.48 | 4.4 | 5 | 0 | 28.9 | 28.4 | 29.2 | 1.51 | 3.7 | 4.6 | 24.9 | 25.1 | 28 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:00:00 | 1.38 | 36.56 | 793795.26 | 765302.04 | 3.24 | 4286.463 | 186.363 | -10.778 | 4 | 177 | 26.2 | 56.8 | 26.4 | 57 | 0 | 0 | - | - | 29.4 | 52.1 | 0 | 0 | 0 | 0 | 29.3 | 29.1 | 29.2 | 1.48 | 4.3 | 4.9 | 0 | 28.8 | 28.4 | 29.2 | 1.51 | 3.7 | 4.5 | 24.9 | 25.1 | 28.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:05:00 | 1.38 | 37.26 | 793795.26 | 765302.7 | 3.31 | 4286.463 | 186.363 | -11.924 | 4 | 177 | 26.2 | 56.8 | 26.4 | 57.1 | 0 | 0 | - | - | 29.4 | 52.1 | 0 | 0 | 0 | 0 | 29.2 | 28.9 | 29.2 | 1.48 | 4.2 | 4.8 | 0 | 28.7 | 28.3 | 29.2 | 1.51 | 3.6 | 4.4 | 24.9 | 25.1 | 28.2 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:10:00 | 1.38 | 38.06 | 793795.26 | 765303.5 | 3.38 | 4301.372 | 171.454 | -8.901 | 4 | 177 | 26.2 | 56.8 | 26.4 | 57 | 0 | 0 | - | - | 29.4 | 52.1 | 0 | 0 | 0 | 0 | 29.2 | 28.9 | 29.1 | 1.48 | 4.2 | 4.7 | 0 | 28.7 | 28.3 | 29.2 | 1.51 | 3.6 | 4.3 | 24.9 | 25.1 | 28.2 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:15:00 | 1.46 | 38.78 | 793795.34 | 765304.2 | 3.44 | 4286.463 | 186.363 | -43.485 | 4 | 177 | 26.3 | 56.8 | 26.4 | 57 | 0 | 0 | - | - | 29.4 | 52.1 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 28.9 | 1.48 | 4.2 | 4.6 | 0 | 28.6 | 28.2 | 29.2 | 1.51 | 3.5 | 4.3 | 24.9 | 25.1 | 28.2 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:20:00 | 1.46 | 39.46 | 793795.34 | 765304.88 | 3.51 | 4286.463 | 186.363 | -9.614 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.4 | 52.2 | 0 | 0 | 0 | 0 | 28.9 | 28.8 | 28.9 | 1.48 | 4 | 4.4 | 0 | 28.6 | 28.2 | 29.2 | 1.51 | 3.5 | 4.2 | 24.9 | 25.1 | 28.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:25:00 | 1.46 | 40.14 | 793795.34 | 765305.56 | 3.57 | 4286.463 | 186.363 | -10.408 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.4 | 52.1 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.8 | 1.48 | 4 | 4.4 | 0 | 28.5 | 28.2 | 29.1 | 1.51 | 3.5 | 4.2 | 25 | 25.1 | 28.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:30:00 | 1.46 | 40.78 | 793795.34 | 765306.2 | 3.64 | 4286.463 | 186.363 | -12.342 | 4 | 177 | 26.3 | 56.8 | 26.4 | 57 | 0 | 0 | - | - | 29.4 | 52.2 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.9 | 1.48 | 3.9 | 4.4 | 0 | 28.5 | 28.2 | 29.1 | 1.51 | 3.4 | 4.2 | 25 | 25.2 | 28.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:35:00 | 1.46 | 41.54 | 793795.34 | 765306.98 | 3.7 | 4308.826 | 164 | -10.486 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.4 | 52.3 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.9 | 1.48 | 3.9 | 4.4 | 0 | 28.5 | 28.2 | 29.1 | 1.51 | 3.5 | 4.2 | 25 | 25.2 | 28.3 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:40:00 | 1.5 | 42.3 | 793795.38 | 765307.72 | 3.77 | 4293.918 | 178.908 | -6.103 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57.1 | 0 | 0 | - | - | 29.4 | 52.3 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.9 | 1.48 | 3.9 | 4.4 | 0 | 28.4 | 28.2 | 29.1 | 1.51 | 3.4 | 4.2 | 25 | 25.2 | 28.3 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:45:00 | 1.52 | 43.02 | 793795.4 | 765308.44 | 3.83 | 4293.918 | 178.908 | -9 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.4 | 52.3 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.9 | 1.49 | 3.9 | 4.4 | 0 | 28.5 | 28.2 | 29.1 | 1.51 | 3.4 | 4.1 | 25 | 25.2 | 28.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:50:00 | 1.52 | 43.72 | 793795.4 | 765309.16 | 3.9 | 4293.918 | 178.908 | -9.453 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.4 | 52.3 | 0 | 0 | 0 | 0 | 29.1 | 28.8 | 29.1 | 1.49 | 4 | 4.6 | 0 | 28.6 | 28.2 | 29.1 | 1.51 | 3.4 | 4.3 | 25 | 25.2 | 27.8 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 04:55:00 | 1.52 | 44.4 | 793795.4 | 765309.84 | 3.96 | 4293.918 | 178.908 | -9.946 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.4 | 52.3 | 0 | 0 | 0 | 0 | 29.2 | 28.9 | 29.4 | 1.48 | 4.1 | 4.8 | 0 | 28.7 | 28.2 | 29.1 | 1.51 | 3.5 | 4.4 | 25 | 25.2 | 27.6 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:00:00 | 1.52 | 45.08 | 793795.4 | 765310.52 | 4.03 | 4293.918 | 178.908 | -9.996 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.3 | 52.3 | 0 | 0 | 0 | 0 | 29.3 | 28.9 | 29.4 | 1.48 | 4.1 | 4.9 | 0 | 28.8 | 28.3 | 29.1 | 1.51 | 3.5 | 4.5 | 25.1 | 25.2 | 27.7 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:05:00 | 1.58 | 45.92 | 793795.46 | 765311.36 | 4.1 | 4316.281 | 156.546 | 18.397 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.3 | 52.3 | 0 | 0 | 0 | 0 | 29.2 | 28.8 | 29.2 | 1.48 | 4 | 4.8 | 0 | 28.7 | 28.2 | 29.1 | 1.51 | 3.5 | 4.4 | 25.1 | 25.2 | 27.8 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:10:00 | 1.64 | 46.66 | 793795.52 | 765312.1 | 4.16 | 4316.281 | 156.546 | -13.137 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.3 | 52.3 | 0 | 0 | 0 | 0 | 29.2 | 28.8 | 29.2 | 1.48 | 4 | 4.6 | 0 | 28.7 | 28.2 | 29.1 | 1.51 | 3.4 | 4.3 | 25.1 | 25.2 | 27.7 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:15:00 | 1.7 | 47.5 | 793795.58 | 765312.94 | 4.23 | 4316.281 | 156.546 | -9.271 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.3 | 52.3 | 0 | 0 | 0 | 0 | 29.2 | 28.8 | 29.1 | 1.48 | 4 | 4.6 | 0 | 28.7 | 28.2 | 29.1 | 1.51 | 3.5 | 4.3 | 25.1 | 25.2 | 27.7 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:20:00 | 1.74 | 48.26 | 793795.62 | 765313.68 | 4.29 | 4316.281 | 156.546 | -3.418 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.3 | 52.4 | 0 | 0 | 0 | 0 | 29.1 | 28.7 | 28.9 | 1.48 | 3.9 | 4.5 | 0 | 28.6 | 28.2 | 29.1 | 1.51 | 3.4 | 4.2 | 25.1 | 25.2 | 27.9 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:25:00 | 1.82 | 49 | 793795.7 | 765314.42 | 4.36 | 4316.281 | 156.546 | -11.492 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.3 | 52.4 | 0 | 0 | 0 | 0 | 29 | 28.8 | 28.9 | 1.49 | 3.9 | 4.5 | 0 | 28.6 | 28.2 | 29.1 | 1.51 | 3.4 | 4.2 | 25.1 | 25.2 | 28.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:30:00 | 1.86 | 49.76 | 793795.74 | 765315.18 | 4.43 | 4316.281 | 156.546 | -12.355 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.3 | 52.4 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.9 | 1.49 | 3.9 | 4.4 | 0 | 28.6 | 28.2 | 29.1 | 1.51 | 3.4 | 4.2 | 25.1 | 25.3 | 28.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:35:00 | 1.94 | 50.48 | 793795.82 | 765315.92 | 4.49 | 4293.918 | 178.908 | -6.928 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57 | 0 | 0 | - | - | 29.3 | 52.4 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 28.8 | 1.49 | 3.9 | 4.4 | 0 | 28.4 | 28.2 | 29.1 | 1.51 | 3.4 | 4.1 | 25.1 | 25.3 | 28 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:40:00 | 1.98 | 51.22 | 793795.86 | 765316.64 | 4.56 | 4301.372 | 171.454 | -10.702 | 4 | 177 | 26.3 | 56.9 | 26.5 | 57 | 0 | 0 | - | - | 29.3 | 52.4 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.8 | 1.49 | 3.9 | 4.3 | 0 | 28.4 | 28.2 | 28.9 | 1.51 | 3.3 | 4.1 | 25.2 | 25.2 | 28.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:45:00 | 1.98 | 51.88 | 793795.86 | 765317.3 | 4.62 | 4301.372 | 171.454 | -9.796 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57.1 | 0 | 0 | - | - | 29.2 | 52.5 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.8 | 1.49 | 3.8 | 4.3 | 0 | 28.4 | 28.2 | 28.9 | 1.51 | 3.3 | 4 | 25.2 | 25.3 | 28.1 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:50:00 | 1.98 | 52.58 | 793795.86 | 765318.02 | 4.69 | 4301.372 | 171.454 | -12.282 | 4 | 177 | 26.3 | 56.8 | 26.4 | 57.2 | 0 | 0 | - | - | 29.3 | 52.5 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 28.7 | 1.49 | 3.7 | 4.2 | 0 | 28.3 | 28.1 | 28.9 | 1.51 | 3.2 | 4 | 25.2 | 25.3 | 28.1 | 1.52 | 1.54 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 05:55:00 | 2.04 | 53.3 | 793795.92 | 765318.72 | 4.76 | 4331.188 | 141.638 | 8.094 | 4 | 177 | 26.3 | 56.8 | 26.4 | 57.3 | 0 | 0 | - | - | 29.3 | 52.5 | 0 | 0 | 0 | 0 | 28.7 | 28.6 | 28.7 | 1.49 | 3.7 | 4.2 | 0 | 28.3 | 28.1 | 28.9 | 1.51 | 3.2 | 4 | 25.2 | 25.3 | 28.1 | 1.52 | 1.54 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:00:00 | 2.04 | 53.92 | 793795.92 | 765319.34 | 4.82 | 4301.372 | 171.454 | -3.063 | 4 | 177 | 26.3 | 56.8 | 26.5 | 57.1 | 0 | 0 | - | - | 29.2 | 52.5 | 0 | 0 | 0 | 0 | 28.7 | 28.6 | 28.7 | 1.49 | 3.7 | 4.1 | 0 | 28.3 | 28.1 | 28.9 | 1.51 | 3.2 | 3.9 | 25.2 | 25.3 | 28.1 | 1.52 | 1.54 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:05:00 | 3.02 | 54.06 | 793796.9 | 765319.48 | 4.88 | 4301.372 | 171.454 | 15.433 | 4 | 177 | 26.4 | 56.8 | 26.6 | 57.1 | 0 | 0 | - | - | 29.2 | 52.6 | 0 | 0 | 0 | 0 | 28.7 | 28.6 | 28.7 | 1.49 | 3.7 | 4.1 | 0 | 28.2 | 28.1 | 28.9 | 1.51 | 3.2 | 3.9 | 25.2 | 25.3 | 28.1 | 1.52 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:10:00 | 5.86 | 54.08 | 793799.74 | 765319.5 | 4.95 | 4301.372 | 171.454 | -0.514 | 4 | 177 | 26.3 | 56.8 | 26.6 | 57 | 0 | 0 | - | - | 29.2 | 52.6 | 0 | 0 | 0 | 0 | 28.7 | 28.6 | 28.6 | 1.49 | 3.6 | 4.1 | 0 | 28.2 | 28.1 | 28.8 | 1.51 | 3.2 | 3.8 | 25.2 | 25.3 | 28.1 | 1.52 | 1.54 | 1.51 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:15:00 | 5.94 | 54.84 | 793799.82 | 765320.26 | 5.01 | 4316.281 | 156.546 | -34.198 | 4 | 177 | 26.3 | 56.8 | 26.6 | 57 | 0 | 0 | - | - | 29.2 | 52.6 | 0 | 0 | 0 | 0 | 28.6 | 28.6 | 28.6 | 1.49 | 3.6 | 4 | 0 | 28.2 | 28.1 | 28.8 | 1.51 | 3.1 | 3.8 | 25.2 | 25.3 | 28.2 | 1.52 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:20:00 | 6.04 | 55.64 | 793799.92 | 765321.08 | 5.07 | 4308.826 | 164 | -43.146 | 4 | 177 | 26.4 | 56.8 | 26.6 | 57 | 0 | 0 | - | - | 29.2 | 52.6 | 0 | 0 | 0 | 0 | 28.6 | 28.5 | 28.6 | 1.49 | 3.6 | 3.9 | 0 | 28.2 | 28.1 | 28.8 | 1.51 | 3.1 | 3.8 | 25.2 | 25.3 | 28.4 | 1.52 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:25:00 | 6.04 | 56.5 | 793799.92 | 765321.98 | 5.14 | 4331.188 | 141.638 | -9.682 | 4 | 177 | 26.4 | 56.8 | 26.6 | 57 | 0 | 0 | - | - | 29.2 | 52.6 | 0 | 0 | 0 | 0 | 28.6 | 28.5 | 28.6 | 1.49 | 3.6 | 4 | 0 | 28.2 | 28.1 | 28.8 | 1.51 | 3.1 | 3.8 | 25.2 | 25.3 | 28.7 | 1.52 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:30:00 | 6.16 | 57.16 | 793800.04 | 765322.58 | 5.2 | 4301.372 | 171.454 | -9.072 | 4 | 177 | 26.4 | 56.7 | 26.5 | 57.2 | 0 | 0 | - | - | 29.2 | 52.6 | 0 | 0 | 0 | 0 | 28.6 | 28.5 | 28.6 | 1.49 | 3.6 | 4 | 0 | 28.3 | 28.1 | 28.9 | 1.51 | 3.1 | 3.9 | 25.2 | 25.4 | 29.1 | 1.52 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:35:00 | 6.16 | 57.82 | 793800.04 | 765323.26 | 5.27 | 4301.372 | 171.454 | -9.575 | 4 | 177 | 26.4 | 56.8 | 26.4 | 57.3 | 0 | 0 | - | - | 29.3 | 52.6 | 0 | 0 | 0 | 0 | 28.6 | 28.5 | 28.7 | 1.49 | 3.6 | 4 | 0 | 28.3 | 28.1 | 29.1 | 1.52 | 3.2 | 3.8 | 25.2 | 25.4 | 29.2 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:40:00 | 6.2 | 58.64 | 793800.08 | 765324.06 | 5.34 | 4331.188 | 141.638 | -6.368 | 4 | 177 | 26.4 | 56.8 | 26.5 | 57.2 | 0 | 0 | - | - | 29.3 | 52.6 | 0 | 0 | 0 | 0 | 28.7 | 28.5 | 28.7 | 1.49 | 3.6 | 4 | 0 | 28.3 | 28.1 | 29.1 | 1.52 | 3.2 | 3.9 | 25.3 | 25.4 | 29.6 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:45:00 | 6.28 | 59.44 | 793800.16 | 765324.86 | 5.4 | 4338.642 | 134.184 | -7.897 | 4 | 177 | 26.4 | 56.9 | 26.6 | 57.1 | 0 | 0 | - | - | 29.4 | 52.6 | 0 | 0 | 0 | 0 | 28.7 | 28.6 | 28.8 | 1.49 | 3.6 | 4 | 0 | 28.3 | 28.1 | 29.2 | 1.52 | 3.2 | 3.8 | 25.3 | 25.4 | 29.9 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:50:00 | 6.38 | 60.16 | 793800.26 | 765325.6 | 5.46 | 4308.826 | 164 | -8.639 | 4 | 177 | 26.4 | 56.8 | 26.6 | 57 | 0 | 0 | - | - | 29.5 | 52.5 | 0 | 0 | 0 | 0 | 28.8 | 28.7 | 29 | 1.49 | 3.6 | 4.1 | 0 | 28.5 | 28.2 | 29.4 | 1.52 | 3.2 | 4 | 25.3 | 25.4 | 30.1 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 06:55:00 | 6.38 | 60.92 | 793800.26 | 765326.34 | 5.52 | 4338.642 | 134.184 | -6.667 | 4 | 177 | 26.5 | 56.7 | 26.7 | 56.9 | 0 | 0 | - | - | 29.5 | 52.4 | 0 | 0 | 0 | 0 | 28.9 | 28.7 | 29.1 | 1.5 | 3.7 | 4.2 | 0 | 28.6 | 28.3 | 29.5 | 1.52 | 3.3 | 4 | 25.3 | 25.4 | 30.1 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:00:00 | 6.4 | 61.64 | 793800.28 | 765327.08 | 5.58 | 4338.642 | 134.184 | -10.985 | 4 | 177 | 26.5 | 56.7 | 26.8 | 56.9 | 0 | 0 | - | - | 29.6 | 52.3 | 0 | 0 | 0 | 0 | 29 | 28.8 | 29.2 | 1.5 | 3.7 | 4.2 | 0 | 28.6 | 28.3 | 29.7 | 1.52 | 3.3 | 4.1 | 25.3 | 25.4 | 30.3 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:05:00 | 6.5 | 62.26 | 793800.38 | 765327.68 | 5.65 | 4338.642 | 134.184 | -9.93 | 4 | 177 | 26.6 | 56.6 | 26.8 | 56.8 | 0 | 0 | - | - | 29.7 | 52.3 | 0 | 0 | 0 | 0 | 29.1 | 28.8 | 29.3 | 1.5 | 3.8 | 4.3 | 0 | 28.7 | 28.4 | 29.8 | 1.52 | 3.4 | 4.1 | 25.3 | 25.4 | 30.6 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:10:00 | 6.52 | 62.86 | 793800.4 | 765328.28 | 5.71 | 4301.372 | 171.454 | -8.423 | 4 | 177 | 26.7 | 56.5 | 26.9 | 56.7 | 0 | 0 | - | - | 29.8 | 52.2 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 29.3 | 1.5 | 3.8 | 4.3 | 0 | 28.7 | 28.4 | 29.9 | 1.52 | 3.4 | 4.1 | 25.3 | 25.5 | 30.9 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:15:00 | 6.54 | 63.64 | 793800.42 | 765329.06 | 5.77 | 4301.372 | 171.454 | -12.045 | 4 | 177 | 26.7 | 56.4 | 26.9 | 56.7 | 0 | 0 | - | - | 29.9 | 52.1 | 0 | 0 | 0 | 0 | 29.2 | 29 | 29.4 | 1.5 | 3.9 | 4.4 | 0 | 28.8 | 28.5 | 30 | 1.52 | 3.5 | 4.2 | 25.3 | 25.5 | 31.1 | 1.53 | 1.55 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:20:00 | 6.54 | 64.32 | 793800.42 | 765329.76 | 5.83 | 4338.642 | 134.184 | -9.78 | 4 | 177 | 26.8 | 56.3 | 27 | 56.6 | 0 | 0 | - | - | 30 | 52.1 | 0 | 0 | 0 | 0 | 29.4 | 29.1 | 29.6 | 1.5 | 4 | 4.5 | 0 | 28.9 | 28.6 | 30.1 | 1.53 | 3.5 | 4.2 | 25.3 | 25.5 | 30.7 | 1.53 | 1.55 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:25:00 | 6.56 | 67.24 | 793800.48 | 765332.66 | 5.9 | 4338.642 | 134.184 | 8.884 | 4 | 177 | 26.9 | 56.2 | 27 | 56.6 | 0 | 0 | - | - | 30.1 | 51.9 | 0 | 0 | 0 | 0 | 29.7 | 29.3 | 29.9 | 1.5 | 4.2 | 4.8 | 0 | 29.2 | 28.7 | 30.3 | 1.53 | 3.7 | 4.5 | 25.3 | 25.5 | 31.4 | 1.54 | 1.55 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:30:00 | 6.72 | 67.66 | 793800.6 | 765333.08 | 5.96 | 4301.372 | 171.454 | -10.503 | 4 | 177 | 27 | 56.1 | 27.1 | 56.5 | 0 | 0 | - | - | 30.2 | 51.8 | 0 | 0 | 0 | 0 | 29.7 | 29.3 | 29.9 | 1.5 | 4.2 | 4.8 | 0 | 29.2 | 28.8 | 30.4 | 1.53 | 3.7 | 4.5 | 25.3 | 25.5 | 31.8 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:35:00 | 6.72 | 68.34 | 793800.6 | 765333.78 | 6.03 | 4338.642 | 134.184 | -5.617 | 4 | 177 | 27.1 | 56 | 27.2 | 56.4 | 0 | 0 | - | - | 30.4 | 51.7 | 0 | 0 | 0 | 0 | 29.7 | 29.4 | 30 | 1.5 | 4.2 | 4.8 | 0 | 29.3 | 28.9 | 30.6 | 1.53 | 3.8 | 4.5 | 25.4 | 25.5 | 32.9 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:40:00 | 6.72 | 69.16 | 793800.6 | 765334.58 | 6.09 | 4301.372 | 171.454 | -11.729 | 4 | 177 | 27.3 | 55.9 | 27.2 | 56.3 | 0 | 0 | - | - | 30.5 | 51.5 | 0 | 0 | 0 | 0 | 29.8 | 29.4 | 30.1 | 1.5 | 4.2 | 4.8 | 0 | 29.3 | 28.9 | 30.8 | 1.53 | 3.8 | 4.6 | 25.4 | 25.6 | 34.2 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:45:00 | 6.76 | 69.86 | 793800.64 | 765335.3 | 6.15 | 4338.642 | 134.184 | -31.559 | 4 | 177 | 27.4 | 55.7 | 27.3 | 56.2 | 0 | 0 | - | - | 30.8 | 51.4 | 0 | 0 | 0 | 0 | 30.1 | 29.7 | 30.5 | 1.51 | 4.4 | 5.1 | 0 | 29.6 | 29.1 | 31.2 | 1.53 | 4 | 4.8 | 25.4 | 25.6 | 34.3 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:50:00 | 6.78 | 70.54 | 793800.66 | 765335.98 | 6.22 | 4331.188 | 141.638 | -7.706 | 4 | 177 | 27.5 | 55.5 | 27.4 | 56.1 | 0 | 0 | - | - | 31.1 | 51.2 | 0 | 0 | 0 | 0 | 30.5 | 30 | 30.9 | 1.51 | 4.7 | 5.5 | 0 | 29.9 | 29.4 | 31.6 | 1.53 | 4.2 | 5.2 | 25.4 | 25.6 | 34.7 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 07:55:00 | 7.04 | 71.36 | 793800.92 | 765336.78 | 6.28 | 4301.372 | 171.454 | -0.781 | 4 | 177 | 27.7 | 55.3 | 27.5 | 56 | 0 | 0 | - | - | 31.4 | 50.9 | 0 | 0 | 0 | 0 | 30.7 | 30.2 | 31.1 | 1.51 | 4.9 | 5.6 | 0 | 30.1 | 29.5 | 31.9 | 1.53 | 4.3 | 5.2 | 25.4 | 25.6 | 34.5 | 1.54 | 1.56 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:00:00 | 7.36 | 72.64 | 793801.26 | 765338.1 | 6.34 | 4338.642 | 134.184 | -1.633 | 4 | 177 | 27.8 | 55.2 | 27.6 | 55.9 | 0 | 0 | - | - | 31.6 | 50.7 | 0 | 0 | 0 | 0 | 30.7 | 30.2 | 31.2 | 1.51 | 4.8 | 5.6 | 0 | 30.1 | 29.6 | 32.1 | 1.53 | 4.4 | 5.3 | 25.4 | 25.6 | 35.1 | 1.55 | 1.56 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:05:00 | 7.78 | 73.42 | 793801.68 | 765338.86 | 6.41 | 4338.642 | 134.184 | -29.846 | 4 | 177 | 28 | 55 | 27.7 | 55.8 | 0 | 0 | - | - | 31.8 | 50.5 | 0 | 0 | 0 | 0 | 31 | 30.4 | 31.5 | 1.51 | 4.9 | 5.9 | 0 | 30.4 | 29.8 | 32.4 | 1.54 | 4.5 | 5.4 | 25.5 | 25.6 | 35.6 | 1.55 | 1.56 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:10:00 | 8.16 | 74.2 | 793802.04 | 765339.62 | 6.47 | 4338.642 | 134.184 | -5.362 | 4 | 177 | 28.2 | 54.8 | 27.9 | 55.7 | 0 | 0 | - | - | 32.1 | 50.2 | 0 | 0 | 0 | 0 | 31.3 | 30.7 | 31.8 | 1.51 | 5.3 | 6.2 | 0 | 30.6 | 30 | 32.7 | 1.54 | 4.7 | 5.7 | 25.5 | 25.7 | 35.7 | 1.55 | 1.56 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:15:00 | 8.52 | 74.88 | 793802.4 | 765340.32 | 6.54 | 4338.642 | 134.184 | -3.961 | 3 | 177 | 28.3 | 54.6 | 28 | 55.5 | 0 | 0 | - | - | 32.4 | 50 | 0 | 0 | 0 | 0 | 31.5 | 30.9 | 31.9 | 1.52 | 5.5 | 6.3 | 0 | 30.8 | 30.2 | 33 | 1.54 | 4.8 | 5.8 | 25.5 | 25.7 | 35.1 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:20:00 | 8.9 | 75.56 | 793802.8 | 765341 | 6.6 | 4338.642 | 134.184 | -3.82 | 3 | 177 | 28.5 | 54.4 | 28.1 | 55.4 | 0 | 0 | - | - | 32.6 | 49.8 | 0 | 0 | 0 | 0 | 31.8 | 31.2 | 32.3 | 1.52 | 5.7 | 6.6 | 0 | 31 | 30.4 | 33.1 | 1.54 | 5.1 | 6.1 | 25.5 | 25.7 | 34.2 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:25:00 | 9.24 | 76.22 | 793803.14 | 765341.64 | 6.66 | 4331.188 | 141.638 | -2.469 | 3 | 177 | 28.7 | 54.2 | 28.2 | 55.3 | 0 | 0 | - | - | 32.8 | 49.6 | 0 | 0 | 0 | 0 | 32 | 31.3 | 32.4 | 1.51 | 5.9 | 6.8 | 0 | 31.3 | 30.6 | 33.2 | 1.54 | 5.2 | 6.3 | 25.5 | 25.7 | 34.9 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:30:00 | 9.66 | 76.92 | 793803.54 | 765342.38 | 6.73 | 4338.642 | 134.184 | -4.632 | 3 | 177 | 28.9 | 54 | 28.3 | 55.2 | 0 | 0 | - | - | 33 | 49.5 | 0 | 0 | 0 | 0 | 32 | 31.3 | 32.5 | 1.52 | 5.8 | 6.8 | 0 | 31.3 | 30.6 | 33.4 | 1.54 | 5.3 | 6.3 | 25.6 | 25.7 | 34.4 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:35:00 | 10.06 | 77.54 | 793803.96 | 765342.96 | 6.79 | 4338.642 | 134.184 | -4.581 | 3 | 177 | 29 | 53.8 | 28.5 | 55 | 0 | 0 | - | - | 33.2 | 49.3 | 0 | 0 | 0 | 0 | 32.3 | 31.5 | 32.6 | 1.52 | 6 | 7.1 | 0 | 31.6 | 30.8 | 33.4 | 1.54 | 5.4 | 6.5 | 25.6 | 25.7 | 33.2 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:40:00 | 10.4 | 78.18 | 793804.3 | 765343.6 | 6.86 | 4338.642 | 134.184 | -7.234 | 3 | 177 | 29.2 | 53.7 | 28.6 | 54.9 | 0 | 0 | - | - | 33.3 | 49.1 | 0 | 0 | 0 | 0 | 32.5 | 31.5 | 32.6 | 1.51 | 6.1 | 7.3 | 0 | 31.7 | 30.9 | 33.4 | 1.54 | 5.5 | 6.7 | 25.6 | 25.7 | 32.9 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:45:00 | 10.76 | 78.84 | 793804.66 | 765344.26 | 6.93 | 4338.642 | 134.184 | -1.16 | 3 | 177 | 29.3 | 53.5 | 28.7 | 54.8 | 0 | 0 | - | - | 33.5 | 49 | 0 | 0 | 0 | 0 | 32.6 | 31.5 | 32.6 | 1.51 | 6.1 | 7.4 | 0 | 31.8 | 30.9 | 33.2 | 1.54 | 5.6 | 6.8 | 25.6 | 25.7 | 32.6 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:50:00 | 11.18 | 79.44 | 793805.06 | 765344.86 | 6.99 | 4331.188 | 141.638 | -10.468 | 3 | 177 | 29.4 | 53.4 | 28.8 | 54.8 | 0 | 0 | - | - | 33.6 | 48.9 | 0 | 0 | 0 | 0 | 32.6 | 31.6 | 32.6 | 1.51 | 6.2 | 7.5 | 0 | 31.9 | 31 | 33.1 | 1.54 | 5.6 | 6.9 | 25.6 | 25.7 | 32.1 | 1.54 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 08:55:00 | 11.56 | 80.12 | 793805.44 | 765345.58 | 7.05 | 4338.642 | 134.184 | -7.258 | 3 | 177 | 29.6 | 53.2 | 28.9 | 54.7 | 0 | 0 | - | - | 33.6 | 48.9 | 0 | 0 | 0 | 0 | 32.6 | 31.4 | 32.4 | 1.51 | 6.1 | 7.6 | 0 | 31.9 | 30.9 | 32.9 | 1.54 | 5.5 | 6.9 | 25.6 | 25.8 | 32.2 | 1.54 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:00:00 | 11.88 | 80.8 | 793805.78 | 765346.26 | 7.12 | 4331.188 | 141.638 | -5.036 | 3 | 177 | 29.7 | 53.1 | 29 | 54.6 | 0 | 0 | - | - | 33.7 | 48.8 | 0 | 0 | 0 | 0 | 32.6 | 31.4 | 32.4 | 1.51 | 6.1 | 7.5 | 0 | 31.9 | 31 | 32.7 | 1.54 | 5.6 | 7 | 25.6 | 25.7 | 31.9 | 1.54 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:05:00 | 12.24 | 81.48 | 793806.14 | 765346.9 | 7.18 | 4331.188 | 141.638 | -5.018 | 3 | 177 | 29.8 | 52.9 | 29.1 | 54.5 | 0 | 0 | - | - | 33.7 | 48.8 | 0 | 0 | 0 | 0 | 32.6 | 31.4 | 32.4 | 1.51 | 6 | 7.5 | 0 | 31.9 | 30.9 | 32.6 | 1.54 | 5.5 | 7 | 25.7 | 25.8 | 32.2 | 1.54 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:10:00 | 12.62 | 82.14 | 793806.5 | 765347.56 | 7.25 | 4338.642 | 134.184 | -0.082 | 3 | 177 | 30 | 52.8 | 29.1 | 54.4 | 0 | 0 | - | - | 33.7 | 48.8 | 0 | 0 | 0 | 0 | 32.6 | 31.4 | 32.4 | 1.51 | 6 | 7.5 | 0 | 32 | 31 | 32.6 | 1.54 | 5.6 | 7 | 25.7 | 25.7 | 32.7 | 1.54 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:15:00 | 13.02 | 82.72 | 793806.9 | 765348.14 | 7.32 | 4331.188 | 141.638 | -13.023 | 3 | 177 | 30.1 | 52.7 | 29.2 | 54.3 | 0 | 0 | - | - | 33.8 | 48.8 | 0 | 0 | 0 | 0 | 32.6 | 31.4 | 32.5 | 1.51 | 6 | 7.6 | 0 | 32 | 31 | 32.7 | 1.54 | 5.6 | 7.1 | 25.7 | 25.8 | 33 | 1.54 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:20:00 | 13.22 | 83.5 | 793807.1 | 765348.94 | 7.38 | 4338.642 | 134.184 | -5.135 | 3 | 177 | 30.2 | 52.6 | 29.3 | 54.2 | 0 | 0 | - | - | 33.8 | 48.7 | 0 | 0 | 0 | 0 | 32.8 | 31.5 | 32.6 | 1.51 | 6.1 | 7.7 | 0 | 32.2 | 31.1 | 32.8 | 1.54 | 5.7 | 7.2 | 25.7 | 25.8 | 33.5 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:25:00 | 13.56 | 84.06 | 793807.46 | 765349.48 | 7.45 | 4331.188 | 141.638 | -7.033 | 3 | 177 | 30.4 | 52.4 | 29.4 | 54.1 | 0 | 0 | - | - | 33.9 | 48.7 | 0 | 0 | 0 | 0 | 32.9 | 31.5 | 32.8 | 1.51 | 6.1 | 7.7 | 0 | 32.2 | 31.2 | 33 | 1.54 | 5.7 | 7.3 | 25.7 | 25.8 | 33.6 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:30:00 | 13.92 | 84.48 | 793807.8 | 765349.9 | 7.52 | 4331.188 | 141.638 | 10.52 | 3 | 177 | 30.5 | 52.3 | 29.5 | 54 | 0 | 0 | - | - | 34 | 48.6 | 0 | 0 | 0 | 0 | 33 | 31.6 | 32.9 | 1.51 | 6.1 | 7.8 | 0 | 32.3 | 31.2 | 33.1 | 1.54 | 5.8 | 7.3 | 25.7 | 25.9 | 33.1 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:35:00 | 14.34 | 84.84 | 793808.24 | 765350.28 | 7.59 | 4331.188 | 141.638 | -3.628 | 3 | 177 | 30.6 | 52.1 | 29.6 | 53.9 | 0 | 0 | - | - | 34.1 | 48.6 | 0 | 0 | 0 | 0 | 33.1 | 31.7 | 32.9 | 1.51 | 6.3 | 7.9 | 0 | 32.4 | 31.2 | 33.1 | 1.54 | 5.8 | 7.5 | 25.8 | 25.9 | 32.8 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:40:00 | 14.68 | 85.4 | 793808.56 | 765350.84 | 7.66 | 4331.188 | 141.638 | -1.642 | 3 | 177 | 30.7 | 52 | 29.7 | 53.8 | 0 | 0 | - | - | 34.1 | 48.5 | 0 | 0 | 0 | 0 | 33.1 | 31.8 | 32.9 | 1.51 | 6.3 | 7.9 | 0 | 32.5 | 31.2 | 33.1 | 1.54 | 5.8 | 7.5 | 25.8 | 25.9 | 33 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:45:00 | 15.02 | 86.02 | 793808.9 | 765351.5 | 7.73 | 4346.097 | 126.729 | -5.75 | 3 | 177 | 30.8 | 51.9 | 29.8 | 53.7 | 0 | 0 | - | - | 34.2 | 48.5 | 0 | 0 | 0 | 0 | 33.2 | 31.8 | 33.1 | 1.52 | 6.3 | 8 | 0 | 32.6 | 31.3 | 33.2 | 1.54 | 5.9 | 7.5 | 25.8 | 25.9 | 33.5 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:50:00 | 15.42 | 86.64 | 793809.3 | 765352.1 | 7.8 | 4346.097 | 126.729 | 0.969 | 3 | 177 | 30.9 | 51.8 | 29.9 | 53.7 | 0 | 0 | - | - | 34.2 | 48.4 | 0 | 0 | 0 | 0 | 33.2 | 31.7 | 33.1 | 1.52 | 6.2 | 8 | 0 | 32.6 | 31.4 | 33.4 | 1.54 | 5.9 | 7.6 | 25.8 | 25.9 | 33.6 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 09:55:00 | 16.1 | 87.2 | 793810 | 765352.62 | 7.88 | 4346.097 | 126.729 | 1.743 | 3 | 177 | 31.1 | 51.7 | 30 | 53.6 | 0 | 0 | - | - | 34.2 | 48.4 | 0 | 0 | 0 | 0 | 33.3 | 31.8 | 33.2 | 1.52 | 6.2 | 8 | 0 | 32.7 | 31.4 | 33.5 | 1.54 | 5.9 | 7.6 | 25.8 | 25.9 | 33.7 | 1.55 | 1.57 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:00:00 | 16.84 | 87.74 | 793810.82 | 765353.16 | 7.95 | 4346.097 | 126.729 | 7.64 | 3 | 177 | 31 | 51.7 | 30.5 | 53 | 0 | 0 | - | - | 34.3 | 48.4 | 0 | 0 | 0 | 0 | 33.5 | 31.9 | 33.4 | 1.52 | 6.3 | 8.2 | 0 | 32.8 | 31.5 | 33.7 | 1.54 | 6 | 7.7 | 25.8 | 26 | 33.3 | 1.55 | 1.57 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:05:00 | 17.96 | 88.14 | 793811.88 | 765353.58 | 8.02 | 4338.642 | 134.184 | 11.429 | 3 | 177 | 31 | 51.8 | 30.8 | 52.6 | 0 | 0 | - | - | 34.3 | 48.4 | 0 | 0 | 0 | 0 | 33.5 | 31.9 | 33.4 | 1.52 | 6.3 | 8.2 | 0 | 32.9 | 31.5 | 33.7 | 1.54 | 5.9 | 7.7 | 25.8 | 26 | 33.3 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:10:00 | 19.32 | 88.4 | 793813.28 | 765353.82 | 8.09 | 4338.642 | 134.184 | 15.796 | 3 | 177 | 31.3 | 51.6 | 30.5 | 53 | 0 | 0 | - | - | 34.4 | 48.3 | 0 | 0 | 0 | 0 | 33.6 | 31.9 | 33.5 | 1.52 | 6.3 | 8.2 | 0 | 32.9 | 31.5 | 33.7 | 1.55 | 6 | 7.8 | 25.9 | 26 | 33.4 | 1.55 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:15:00 | 20.74 | 88.7 | 793814.66 | 765354.12 | 8.17 | 4338.642 | 134.184 | 12.007 | 3 | 177 | 31.4 | 51.4 | 30.4 | 53.2 | 0 | 0 | - | - | 34.4 | 48.3 | 0 | 0 | 0 | 0 | 33.6 | 32 | 33.5 | 1.52 | 6.4 | 8.3 | 0 | 33 | 31.6 | 33.8 | 1.55 | 6 | 7.9 | 25.9 | 26 | 33.8 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:20:00 | 22.18 | 88.96 | 793816.1 | 765354.38 | 8.24 | 4331.188 | 141.638 | 8.249 | 3 | 177 | 31.6 | 51.2 | 30.4 | 53.1 | 0 | 0 | - | - | 34.5 | 48.3 | 0 | 0 | 0 | 0 | 33.7 | 32.1 | 33.6 | 1.52 | 6.4 | 8.3 | 0 | 33.1 | 31.7 | 33.9 | 1.55 | 6.1 | 7.9 | 25.8 | 26 | 34.2 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:25:00 | 23.5 | 89.28 | 793817.44 | 765354.7 | 8.31 | 4338.642 | 134.184 | 13.025 | 3 | 177 | 31.7 | 51.1 | 30.5 | 53.1 | 0 | 0 | - | - | 34.6 | 48.2 | 0 | 0 | 0 | 0 | 33.9 | 32.2 | 33.8 | 1.52 | 6.6 | 8.5 | 0 | 33.2 | 31.8 | 34.1 | 1.55 | 6.2 | 8 | 25.9 | 26.1 | 34.1 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:30:00 | 24.9 | 89.58 | 793818.84 | 765355.02 | 8.39 | 4338.642 | 134.184 | 15.871 | 3 | 177 | 31.8 | 51 | 30.6 | 53 | 0 | 0 | - | - | 34.6 | 48.2 | 0 | 0 | 0 | 0 | 34 | 32.4 | 33.9 | 1.52 | 6.7 | 8.6 | 0 | 33.3 | 31.8 | 34.2 | 1.55 | 6.2 | 8.1 | 25.9 | 26.1 | 34.1 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:35:00 | 26.36 | 89.9 | 793820.24 | 765355.32 | 8.46 | 4338.642 | 134.184 | 12.31 | 4 | 177 | 32 | 50.8 | 30.7 | 52.9 | 0 | 0 | - | - | 34.7 | 48.1 | 0 | 0 | 0 | 0 | 34.1 | 32.4 | 33.9 | 1.52 | 6.7 | 8.7 | 0 | 33.4 | 31.9 | 34.2 | 1.55 | 6.3 | 8.2 | 25.9 | 26.1 | 34.1 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:40:00 | 27.78 | 90.16 | 793821.68 | 765355.6 | 8.54 | 4331.188 | 141.638 | 11.57 | 4 | 177 | 32.3 | 50.6 | 30.8 | 52.9 | 0 | 0 | - | - | 34.8 | 48.1 | 0 | 0 | 0 | 0 | 34.2 | 32.4 | 34 | 1.53 | 6.7 | 8.8 | 0 | 33.5 | 32 | 34.3 | 1.55 | 6.4 | 8.2 | 25.9 | 26.1 | 34.2 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:45:00 | 29.1 | 90.58 | 793822.98 | 765356 | 8.62 | 4331.188 | 141.638 | 11.432 | 4 | 177 | 32.7 | 50.2 | 30.8 | 52.9 | 0 | 0 | - | - | 34.9 | 48 | 0 | 0 | 0 | 0 | 34.2 | 32.5 | 34.1 | 1.53 | 6.8 | 8.8 | 0 | 33.5 | 32.1 | 34.4 | 1.55 | 6.4 | 8.2 | 26 | 26.1 | 34 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:50:00 | 30.22 | 91.04 | 793824.12 | 765356.46 | 8.7 | 4338.642 | 134.184 | 21.019 | 4 | 177 | 32.7 | 50.1 | 30.8 | 52.8 | 0 | 0 | - | - | 35 | 48 | 0 | 0 | 0 | 0 | 34.2 | 32.5 | 34.2 | 1.53 | 6.7 | 8.7 | 0 | 33.6 | 32.1 | 34.5 | 1.55 | 6.4 | 8.2 | 26 | 26.1 | 34.6 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 10:55:00 | 31.32 | 91.48 | 793825.22 | 765356.9 | 8.78 | 4338.642 | 134.184 | 11.185 | 4 | 177 | 32.6 | 50.3 | 30.9 | 52.8 | 0 | 0 | - | - | 35 | 47.9 | 0 | 0 | 0 | 0 | 34.3 | 32.4 | 34.2 | 1.53 | 6.7 | 8.8 | 0 | 33.6 | 32.2 | 34.6 | 1.55 | 6.5 | 8.3 | 26 | 26.2 | 34.8 | 1.56 | 1.57 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:00:00 | 41.84 | 91.68 | 793837.78 | 765357.1 | 8.87 | 4331.188 | 141.638 | 400.34 | 4 | 177 | 32.6 | 50.3 | 31 | 52.7 | 0 | 0 | - | - | 35.1 | 47.9 | 0 | 0 | 0 | 0 | 34.3 | 32.6 | 34.4 | 1.53 | 6.7 | 8.8 | 0 | 33.7 | 32.3 | 34.9 | 1.56 | 6.5 | 8.4 | 26 | 26.2 | 35.2 | 1.56 | 1.58 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:05:00 | 96.86 | 91.68 | 793892.3 | 765357.1 | 8.97 | 4279.009 | 193.818 | 1016.261 | 5 | 177 | 32.7 | 50.2 | 31.1 | 52.6 | 0 | 0 | - | - | 35.2 | 47.7 | 0 | 0 | 0 | 0 | 34.6 | 32.7 | 34.7 | 1.53 | 6.9 | 9.1 | 0 | 33.9 | 32.5 | 35.1 | 1.55 | 6.7 | 8.6 | 26 | 26.2 | 35.3 | 1.56 | 1.58 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:10:00 | 189.56 | 91.68 | 793985.36 | 765357.1 | 9.08 | 4197.003 | 275.823 | 1210.429 | 7 | 177 | 32.7 | 50.2 | 31.2 | 52.5 | 0 | 0 | - | - | 35.3 | 47.7 | 0 | 0 | 0 | 0 | 34.8 | 32.9 | 35 | 1.53 | 7.1 | 9.3 | 0 | 34.1 | 32.6 | 35.3 | 1.55 | 6.9 | 8.8 | 25.9 | 26.1 | 35.6 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:15:00 | 292.48 | 91.68 | 794087.6 | 765357.1 | 9.19 | 4100.094 | 372.732 | 1215.529 | 10 | 177 | 32.9 | 50.1 | 31.3 | 52.5 | 0 | 0 | - | - | 35.5 | 47.6 | 0 | 0 | 0 | 0 | 34.9 | 33 | 35.2 | 1.53 | 7.3 | 9.5 | 0 | 34.2 | 32.7 | 35.5 | 1.55 | 7 | 8.9 | 25.9 | 26.1 | 34.9 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:20:00 | 394.66 | 91.68 | 794191.1 | 765357.1 | 9.31 | 4003.182 | 469.644 | 1230.449 | 12 | 177 | 33.1 | 49.9 | 31.5 | 52.4 | 0 | 0 | - | - | 35.6 | 47.5 | 0 | 0 | 0 | 0 | 35.1 | 33.1 | 35.3 | 1.53 | 7.4 | 9.6 | 0 | 34.4 | 32.8 | 35.6 | 1.55 | 7.1 | 9.1 | 26 | 26.2 | 35.2 | 1.56 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:25:00 | 498.08 | 91.68 | 794295.2 | 765357.1 | 9.43 | 3906.27 | 566.556 | 1238.368 | 14 | 177 | 33.3 | 49.9 | 31.6 | 52.3 | 0 | 0 | - | - | 35.7 | 47.4 | 0 | 0 | 0 | 0 | 35.3 | 33.3 | 35.4 | 1.53 | 7.5 | 9.8 | 0 | 34.5 | 32.9 | 35.7 | 1.55 | 7.1 | 9.2 | 26.2 | 26.4 | 35.1 | 1.56 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:30:00 | 601.54 | 91.68 | 794396.66 | 765357.1 | 9.55 | 3816.814 | 656.012 | 1236.178 | 16 | 177 | 33.4 | 49.7 | 31.7 | 52.2 | 0 | 0 | - | - | 35.8 | 47.4 | 0 | 0 | 0 | 0 | 35.4 | 33.4 | 35.4 | 1.53 | 7.4 | 9.8 | 0 | 34.6 | 32.9 | 35.7 | 1.56 | 6.9 | 9.2 | 26.4 | 26.6 | 34.9 | 1.57 | 1.59 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:35:00 | 729.04 | 91.68 | 794526.06 | 765357.1 | 9.68 | 3697.538 | 775.288 | 2063.256 | 19 | 177 | 33.6 | 49.6 | 31.8 | 52.2 | 0 | 0 | - | - | 35.9 | 47.3 | 0 | 0 | 0 | 0 | 35.5 | 33.5 | 35.4 | 1.54 | 7.4 | 9.8 | 0 | 34.7 | 33.1 | 35.7 | 1.56 | 6.9 | 9.3 | 26.6 | 26.7 | 35.1 | 1.57 | 1.59 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:40:00 | 899.4 | 91.68 | 794696.4 | 765357.1 | 10.01 | 3540.988 | 931.838 | 2061.883 | 23 | 177 | 33.9 | 49.5 | 32 | 52.1 | 0 | 0 | - | - | 36.1 | 47.3 | 193 | 186 | 43.1 | 43.8 | 46.8 | 27.2 | 40.3 | 2.63 | 20.3 | -0.2 | 43.2 | 45.6 | 26.4 | 41 | 2.73 | 17 | -2.5 | 24.3 | 26.7 | 35 | 2.54 | 1.05 | 2.73 | 1.14 | 224 | 194 | 2631 | 2631
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:45:00 | 1072.6 | 91.68 | 794868.6 | 765357.1 | 10.88 | 3376.986 | 1095.843 | 2071.894 | 27 | 177 | 34.1 | 49.2 | 32.3 | 51.8 | 0 | 0 | - | - | 36.2 | 47.2 | 228 | 189 | 65.1 | 65 | 70.2 | 24.3 | 44.3 | 2.57 | 11.3 | 24.7 | 64.6 | 73.2 | 24.2 | 47.6 | 2.82 | 9.7 | 24.3 | 22.1 | 24.2 | 34.3 | 2.59 | 1.07 | 2.83 | 1.13 | 228 | 189 | 2721 | 2721
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:50:00 | 1246.1 | 91.68 | 795043.16 | 765357.1 | 11.76 | 3190.618 | 1282.208 | 2074.262 | 31 | 177 | 34.2 | 49 | 32.5 | 51.4 | 0 | 0 | - | - | 36.4 | 47 | 228 | 189 | 64 | 64.5 | 72 | 23.3 | 43.9 | 2.51 | 10.8 | 27.3 | 64.5 | 74.9 | 23.3 | 47.6 | 2.79 | 9.4 | 26.5 | 21.6 | 23.4 | 35 | 2.64 | 1.06 | 2.84 | 1.1 | 228 | 189 | 2499 | 2499
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 11:55:00 | 1418.2 | 91.68 | 795216.5 | 765357.1 | 12.57 | 3034.066 | 1438.76 | 2060.344 | 34 | 177 | 34.5 | 48.6 | 32.8 | 51 | 0 | 0 | - | - | 36.6 | 46.9 | 228 | 189 | 63.1 | 63.2 | 71.6 | 23.4 | 43.8 | 2.49 | 10.4 | 27.2 | 62.8 | 75.1 | 23.3 | 47.4 | 2.77 | 9.4 | 27 | 21.7 | 23.6 | 35.4 | 2.57 | 1.08 | 2.79 | 1.11 | 228 | 189 | 2383 | 2383
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:00:00 | 1583.56 | 91.68 | 795384.88 | 765357.1 | 13.35 | 2884.974 | 1587.852 | 2063.165 | 38 | 177 | 34.8 | 48.3 | 33 | 50.7 | 0 | 0 | - | - | 36.8 | 46.7 | 228 | 189 | 62.6 | 62.6 | 70.7 | 23.6 | 43.6 | 2.47 | 10.5 | 26.7 | 62.4 | 74.3 | 23.5 | 47 | 2.76 | 9.4 | 26.4 | 21.9 | 23.8 | 35.3 | 2.57 | 1.08 | 2.81 | 1.11 | 228 | 189 | 2391 | 2391
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:05:00 | 1762.44 | 91.68 | 795557.38 | 765357.1 | 14.14 | 2728.423 | 1744.403 | 2062.853 | 42 | 177 | 35 | 48.2 | 33.3 | 50.5 | 0 | 0 | - | - | 37 | 46.6 | 228 | 189 | 63.8 | 63.9 | 71.2 | 23.8 | 44 | 2.55 | 10.8 | 25.9 | 63.6 | 74.8 | 23.8 | 47.4 | 2.8 | 9.5 | 26.2 | 22.2 | 24.1 | 36 | 2.64 | 1.08 | 2.85 | 1.12 | 228 | 189 | 2391 | 2391
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:10:00 | 1935.96 | 91.68 | 795730.88 | 765357.1 | 14.94 | 2549.513 | 1923.313 | 2061.813 | 46 | 177 | 35.3 | 48 | 33.6 | 50.3 | 0 | 0 | - | - | 37.2 | 46.5 | 228 | 189 | 63.3 | 63.2 | 70.9 | 24.2 | 43.6 | 2.52 | 10.8 | 26.1 | 63.5 | 74.8 | 24.2 | 47.4 | 2.8 | 9.5 | 26.3 | 22.5 | 24.5 | 36.4 | 2.58 | 1.1 | 2.84 | 1.14 | 228 | 189 | 2391 | 2391
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:15:00 | 2097.48 | 91.68 | 795895.6 | 765357.1 | 15.74 | 2392.962 | 2079.864 | 1940.541 | 49 | 177 | 35.5 | 47.9 | 33.9 | 50.1 | 0 | 0 | - | - | 37.5 | 46.3 | 228 | 189 | 64.9 | 64.8 | 71.8 | 24.6 | 44.7 | 2.58 | 10.9 | 26.2 | 65.1 | 75.2 | 24.6 | 48 | 2.84 | 9.6 | 26.1 | 23 | 24.9 | 37.6 | 2.63 | 1.11 | 2.87 | 1.15 | 228 | 189 | 2391 | 2391
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:20:00 | 2250.62 | 91.68 | 796045.32 | 765357.1 | 16.55 | 2266.232 | 2206.595 | 1648.834 | 52 | 177 | 35.8 | 47.8 | 34.2 | 49.9 | 0 | 0 | - | - | 37.7 | 46.2 | 228 | 189 | 64.5 | 64.6 | 71.6 | 25.1 | 44 | 2.54 | 11 | 26.5 | 64.1 | 75.4 | 25 | 47.9 | 2.84 | 9.7 | 26.3 | 23.4 | 25.3 | 37.5 | 2.62 | 1.12 | 2.87 | 1.16 | 228 | 189 | 2391 | 2391
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:25:00 | 2385.42 | 91.68 | 796182.8 | 765357.1 | 17.38 | 2102.227 | 2370.599 | 1674.343 | 55 | 178 | 36.1 | 47.7 | 34.5 | 49.7 | 0 | 0 | - | - | 37.9 | 46 | 228 | 189 | 66.5 | 66.6 | 72.9 | 25.5 | 45.4 | 2.6 | 11 | 26.9 | 66.3 | 76.3 | 25.4 | 48.7 | 2.87 | 9.8 | 26.7 | 23.7 | 25.7 | 37.9 | 2.64 | 1.13 | 2.9 | 1.17 | 228 | 189 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:30:00 | 2524.12 | 91.68 | 796322.28 | 765357.1 | 18.21 | 1975.497 | 2497.329 | 1678.617 | 58 | 178 | 36.3 | 47.6 | 34.9 | 49.5 | 0 | 0 | - | - | 38.1 | 46 | 228 | 189 | 66 | 66.5 | 72.4 | 25.8 | 44.7 | 2.56 | 11.3 | 27 | 66.3 | 76 | 25.7 | 48.7 | 2.87 | 9.7 | 26.4 | 24 | 26 | 37.8 | 2.66 | 1.13 | 2.92 | 1.19 | 228 | 189 | 2502 | 2502
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:35:00 | 2650.78 | 91.68 | 796447.16 | 765357.1 | 19.08 | 1863.678 | 2609.148 | 1233.413 | 61 | 178 | 36.6 | 47.5 | 35.2 | 49.3 | 0 | 0 | - | - | 38.3 | 45.9 | 230 | 189 | 67.5 | 67.6 | 73.9 | 26.1 | 45.9 | 2.65 | 11.5 | 27 | 68 | 76.6 | 26 | 48.9 | 2.92 | 9.9 | 26.3 | 24.2 | 26.3 | 38 | 2.73 | 1.13 | 2.97 | 1.19 | 230 | 189 | 2509 | 2509
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:40:00 | 2753.54 | 91.68 | 796549.42 | 765357.1 | 19.99 | 1766.766 | 2706.06 | 1265.247 | 63 | 178 | 36.9 | 47.4 | 35.5 | 49.2 | 0 | 0 | - | - | 38.5 | 45.8 | 233 | 189 | 68.8 | 68.8 | 74.1 | 26.3 | 45.9 | 2.66 | 11.4 | 27.2 | 69.1 | 77.1 | 26.2 | 49.6 | 2.95 | 9.6 | 26.4 | 24.3 | 26.4 | 37.9 | 2.69 | 1.14 | 2.97 | 1.2 | 233 | 189 | 2655 | 2655
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:45:00 | 2857.1 | 91.68 | 796653.62 | 765357.1 | 20.93 | 1647.489 | 2825.337 | 1247.405 | 65 | 178 | 37.2 | 47.3 | 35.7 | 49.1 | 0 | 0 | - | - | 38.7 | 45.7 | 234 | 189 | 69.7 | 69.4 | 74.3 | 26.3 | 46.1 | 2.66 | 11.4 | 27.4 | 69.4 | 77.1 | 26.2 | 49.8 | 2.97 | 9.5 | 26.1 | 24.4 | 26.5 | 38.6 | 2.74 | 1.14 | 3 | 1.2 | 234 | 189 | 2643 | 2643
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:50:00 | 2960.2 | 91.68 | 796755.12 | 765357.1 | 21.88 | 1558.035 | 2914.791 | 1029.639 | 68 | 178 | 37.4 | 47.2 | 36 | 49 | 0 | 0 | - | - | 38.9 | 45.7 | 235 | 189 | 69.7 | 70 | 74.4 | 26.4 | 45.9 | 2.68 | 11.5 | 27.1 | 70 | 77.2 | 26.3 | 49.9 | 2.98 | 9.6 | 26.1 | 24.5 | 26.6 | 38.9 | 2.75 | 1.15 | 3.01 | 1.21 | 236 | 189 | 2664 | 2664
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 12:55:00 | 3022.3 | 91.68 | 796816.6 | 765357.1 | 22.83 | 1490.94 | 2981.886 | 179.864 | 69 | 178 | 37.6 | 47.1 | 36.1 | 49 | 0 | 0 | - | - | 39 | 45.6 | 236 | 189 | 70 | 70 | 74.4 | 26.4 | 46.2 | 2.69 | 11.4 | 27.1 | 70 | 77.1 | 26.3 | 50 | 2.99 | 9.5 | 25.9 | 24.5 | 26.6 | 39.6 | 2.76 | 1.15 | 3.04 | 1.21 | 237 | 189 | 2721 | 2728
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:00:00 | 3036.24 | 91.84 | 796830.12 | 765357.36 | 23.83 | 1468.576 | 3004.25 | -13.952 | 69 | 178 | 38.1 | 46.7 | 36.2 | 48.9 | 0 | 0 | - | - | 39.2 | 45.5 | 238 | 189 | 73.3 | 73.4 | 75.6 | 26.3 | 47.1 | 2.72 | 11.3 | 27.7 | 73.3 | 78 | 26.2 | 50.7 | 3.04 | 9 | 26 | 24.2 | 26.4 | 39.9 | 2.8 | 1.14 | 3.09 | 1.23 | 238 | 189 | 2875 | 2832
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:05:00 | 3039.22 | 93.2 | 796833.32 | 765358.62 | 24.85 | 1468.576 | 3004.25 | 204.188 | 69 | 178 | 38.4 | 46.4 | 36.3 | 48.7 | 0 | 0 | - | - | 39.2 | 45.5 | 238 | 189 | 72.9 | 72.2 | 75.1 | 26.1 | 46.6 | 2.67 | 11.1 | 27.9 | 72.3 | 77.1 | 25.9 | 50.4 | 3.02 | 8.5 | 25.3 | 23.9 | 26.2 | 39.6 | 2.74 | 1.14 | 3.06 | 1.23 | 238 | 189 | 2868 | 2868
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:10:00 | 3077.2 | 93.2 | 796872.02 | 765358.62 | 25.88 | 1438.76 | 3034.066 | 623.497 | 70 | 178 | 38.3 | 46.5 | 36.2 | 48.8 | 0 | 0 | - | - | 39.2 | 45.5 | 238 | 189 | 71.8 | 71.7 | 74.4 | 25.8 | 46.3 | 2.69 | 11.2 | 27.1 | 71.8 | 76.6 | 25.7 | 50.1 | 3.01 | 8.6 | 25 | 23.7 | 25.9 | 39.1 | 2.75 | 1.14 | 3.05 | 1.22 | 238 | 189 | 2868 | 2868
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:15:00 | 3135.22 | 93.2 | 796930.82 | 765358.62 | 26.92 | 1371.666 | 3101.16 | 823.09 | 71 | 178 | 38.2 | 46.5 | 36.1 | 48.9 | 0 | 0 | - | - | 39.2 | 45.6 | 238 | 189 | 72.4 | 72.4 | 75 | 25.6 | 46.6 | 2.71 | 11.1 | 27.3 | 72.4 | 77.1 | 25.6 | 50.4 | 3.02 | 8.7 | 25.3 | 23.6 | 25.7 | 39.7 | 2.77 | 1.13 | 3.06 | 1.21 | 238 | 189 | 2868 | 2868
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:20:00 | 3203.06 | 93.2 | 796998.24 | 765358.62 | 27.97 | 1312.027 | 3160.799 | 818.922 | 73 | 178 | 38.1 | 46.5 | 36 | 49 | 0 | 0 | - | - | 39.2 | 45.6 | 238 | 189 | 72.4 | 72.9 | 75.5 | 25.4 | 46.9 | 2.73 | 11.2 | 27.5 | 72.9 | 77.4 | 25.3 | 50.4 | 3.03 | 8.8 | 25.6 | 23.4 | 25.7 | 38.9 | 2.72 | 1.13 | 3.04 | 1.21 | 238 | 189 | 2868 | 2868
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:25:00 | 3271.74 | 93.2 | 797067.8 | 765358.62 | 28.97 | 1237.482 | 3235.344 | 833.445 | 74 | 178 | 38 | 46.6 | 35.9 | 49.1 | 0 | 0 | - | - | 39 | 45.7 | 238 | 185 | 70.1 | 70.2 | 73.1 | 25.2 | 45.1 | 2.59 | 11 | 27.1 | 70.2 | 75.6 | 25.1 | 49.3 | 2.95 | 8.4 | 24.8 | 23.1 | 25.3 | 37 | 2.67 | 1.12 | 2.99 | 1.2 | 238 | 185 | 2868 | 2868
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:30:00 | 3350.48 | 93.2 | 797145.46 | 765358.62 | 29.98 | 1162.933 | 3309.894 | 1055.183 | 76 | 178 | 37.8 | 46.6 | 35.7 | 49.1 | 0 | 0 | - | - | 38.9 | 45.8 | 238 | 184 | 69.6 | 69.6 | 72.9 | 24.9 | 45.1 | 2.58 | 10.9 | 27.2 | 69.6 | 75.4 | 24.8 | 48.9 | 2.94 | 8.4 | 24.8 | 22.9 | 25.1 | 36.4 | 2.7 | 1.11 | 2.99 | 1.19 | 238 | 184 | 2868 | 2868
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:35:00 | 3438.64 | 93.2 | 797235.14 | 765358.62 | 30.98 | 1066.023 | 3406.803 | 1252.378 | 78 | 178 | 37.6 | 46.7 | 35.5 | 49.3 | 0 | 0 | - | - | 38.7 | 45.9 | 238 | 183 | 69.1 | 69 | 73 | 24.8 | 45.1 | 2.59 | 10.9 | 27.1 | 68.9 | 75.4 | 24.7 | 48.9 | 2.93 | 8.5 | 24.9 | 22.7 | 25 | 36.1 | 2.66 | 1.11 | 2.97 | 1.19 | 238 | 183 | 2868 | 2868
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:40:00 | 3543.44 | 93.2 | 797340.58 | 765358.62 | 31.97 | 969.11 | 3503.716 | 1271.064 | 80 | 178 | 37.3 | 46.9 | 35.3 | 49.4 | 0 | 0 | - | - | 38.5 | 46.1 | 238 | 180 | 68.5 | 68.5 | 72.4 | 24.7 | 44.6 | 2.57 | 10.8 | 26.8 | 68.4 | 75.2 | 24.6 | 48.7 | 2.92 | 8.5 | 24.8 | 22.7 | 24.8 | 35.4 | 2.63 | 1.11 | 2.95 | 1.19 | 238 | 180 | 2868 | 2868
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:45:00 | 3649.86 | 93.2 | 797446.36 | 765358.62 | 32.96 | 849.834 | 3622.992 | 1279.266 | 82 | 178 | 37 | 47.2 | 35 | 49.6 | 0 | 0 | - | - | 38.3 | 46.2 | 238 | 178 | 68.7 | 68.6 | 72.8 | 24.6 | 44.9 | 2.56 | 10.7 | 27.3 | 68.4 | 75.4 | 24.4 | 48.8 | 2.91 | 8.6 | 25.1 | 22.6 | 24.7 | 35.8 | 2.63 | 1.1 | 2.94 | 1.18 | 238 | 178 | 2868 | 2868
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:50:00 | 3750.3 | 93.2 | 797545.1 | 765358.62 | 33.93 | 760.379 | 3712.447 | 874.822 | 84 | 178 | 36.6 | 47.4 | 34.8 | 49.8 | 0 | 0 | - | - | 38.1 | 46.4 | 238 | 176 | 67.5 | 67.6 | 72 | 24.4 | 44.2 | 2.54 | 10.7 | 26.9 | 67.3 | 74.9 | 24.4 | 48.4 | 2.89 | 8.6 | 24.8 | 22.4 | 24.7 | 34.2 | 2.6 | 1.1 | 2.93 | 1.18 | 238 | 175 | 2856 | 2856
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 13:55:00 | 3790.84 | 93.3 | 797584.72 | 765358.74 | 34.87 | 730.56 | 3742.266 | -13.838 | 85 | 178 | 36.1 | 47.7 | 34.5 | 49.9 | 0 | 0 | - | - | 37.9 | 46.5 | 238 | 155 | 64.2 | 64.4 | 69 | 24.2 | 42.2 | 2.44 | 10.5 | 25.4 | 64.7 | 72.6 | 24.2 | 46.6 | 2.82 | 8.2 | 23.6 | 22.2 | 24.4 | 31.4 | 2.52 | 1.1 | 2.86 | 1.18 | 238 | 154 | 2838 | 2838
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:00:00 | 3790.84 | 94.34 | 797584.72 | 765359.8 | 35.76 | 730.56 | 3742.266 | -15.07 | 85 | 178 | 36.1 | 47.7 | 34.3 | 50 | 0 | 0 | - | - | 37.5 | 46.7 | 238 | 150 | 61.4 | 61.5 | 67.4 | 23.9 | 41.1 | 2.33 | 10.2 | 25.6 | 61.2 | 72 | 23.8 | 44.2 | 2.73 | 8.5 | 24.4 | 21.8 | 24.2 | 29.4 | 2.41 | 1.1 | 2.76 | 1.16 | 238 | 150 | 2838 | 2838
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:05:00 | 3802.44 | 94.68 | 797596.6 | 765360.1 | 36.63 | 685.83 | 3786.996 | 195.198 | 85 | 178 | 35.7 | 47.8 | 33.8 | 50.3 | 0 | 0 | - | - | 37.2 | 47 | 238 | 149 | 60.3 | 60.7 | 66.7 | 23.7 | 40.9 | 2.33 | 10.3 | 24.9 | 60.6 | 71.1 | 23.6 | 44.1 | 2.71 | 8.4 | 23.9 | 21.7 | 23.8 | 28.9 | 2.39 | 1.09 | 2.74 | 1.15 | 238 | 148 | 2758 | 2766
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:10:00 | 3818.44 | 94.68 | 797612.72 | 765360.1 | 37.44 | 685.83 | 3786.996 | 194.111 | 86 | 178 | 34.8 | 48.5 | 33.7 | 50.3 | 0 | 0 | - | - | 36.7 | 47.3 | 238 | 145 | 58.3 | 58.5 | 65.7 | 23.5 | 40.1 | 2.3 | 10.2 | 24.4 | 58.6 | 70.5 | 23.4 | 44.4 | 2.66 | 8.7 | 24.1 | 21.7 | 23.7 | 28.7 | 2.35 | 1.09 | 2.69 | 1.14 | 238 | 145 | 2610 | 2611
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:15:00 | 3834.74 | 94.68 | 797629 | 765360.1 | 38.21 | 678.375 | 3794.451 | 419.034 | 86 | 178 | 34 | 49.2 | 33.4 | 50.3 | 0 | 0 | - | - | 36.2 | 47.6 | 238 | 145 | 57.3 | 57.4 | 65.5 | 23.4 | 40.1 | 2.3 | 10.2 | 24.4 | 57.1 | 70.7 | 23.5 | 44.6 | 2.64 | 9.1 | 24.6 | 21.7 | 23.7 | 28.9 | 2.37 | 1.08 | 2.67 | 1.12 | 238 | 145 | 2541 | 2550
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:20:00 | 3869.64 | 94.68 | 797664 | 765360.1 | 38.96 | 641.104 | 3831.722 | 432.502 | 87 | 178 | 33.7 | 49.5 | 32.9 | 50.8 | 0 | 0 | - | - | 35.8 | 48 | 238 | 145 | 55.7 | 55.8 | 65.1 | 23.4 | 39.6 | 2.26 | 10.3 | 24.6 | 55.5 | 70.5 | 23.4 | 44.1 | 2.61 | 9.5 | 24.8 | 21.7 | 23.7 | 26.6 | 2.31 | 1.09 | 2.61 | 1.12 | 238 | 145 | 2439 | 2436
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:25:00 | 3905.1 | 94.68 | 797700.12 | 765360.1 | 39.66 | 611.286 | 3861.54 | 430.176 | 88 | 178 | 33.3 | 49.7 | 32.4 | 51.3 | 0 | 0 | - | - | 35.3 | 48.3 | 238 | 145 | 54 | 54 | 64 | 23.3 | 39.1 | 2.22 | 10.2 | 24 | 54.2 | 69.8 | 23.3 | 43.4 | 2.56 | 9.7 | 25 | 21.7 | 23.7 | 25.7 | 2.29 | 1.09 | 2.57 | 1.1 | 238 | 145 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:30:00 | 3940.94 | 94.68 | 797735.5 | 765360.1 | 40.34 | 574.011 | 3898.815 | 423.119 | 88 | 178 | 32.9 | 50.1 | 31.9 | 51.8 | 0 | 0 | - | - | 34.6 | 48.8 | 238 | 145 | 52.8 | 52.8 | 63.2 | 23.2 | 38.6 | 2.2 | 10.1 | 23.6 | 52.9 | 69.3 | 23.2 | 43.1 | 2.53 | 9.6 | 24.9 | 21.6 | 23.5 | 25.1 | 2.27 | 1.08 | 2.55 | 1.1 | 238 | 145 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:35:00 | 3984.26 | 94.68 | 797779.74 | 765360.1 | 41.03 | 536.736 | 3936.09 | 640.36 | 89 | 178 | 32.4 | 50.4 | 31.4 | 52.2 | 0 | 0 | - | - | 33.9 | 49.3 | 238 | 145 | 51.7 | 51.8 | 62.8 | 23.1 | 38.1 | 2.18 | 10 | 23.5 | 51.8 | 68.8 | 23.1 | 42.6 | 2.51 | 9.6 | 24.8 | 21.3 | 23.3 | 24.8 | 2.26 | 1.07 | 2.55 | 1.1 | 238 | 145 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:40:00 | 4038.66 | 94.68 | 797834.22 | 765360.1 | 41.72 | 484.552 | 3988.274 | 641.497 | 91 | 178 | 32 | 50.7 | 31 | 52.5 | 0 | 0 | - | - | 33.2 | 49.9 | 238 | 145 | 52.6 | 52.3 | 62.7 | 22.9 | 38.2 | 2.18 | 10.2 | 23.5 | 52.3 | 68.9 | 22.9 | 42.7 | 2.52 | 9.6 | 24.8 | 21.2 | 23.2 | 24.7 | 2.27 | 1.07 | 2.55 | 1.09 | 238 | 145 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:45:00 | 4094.56 | 94.68 | 797889.1 | 765360.1 | 42.41 | 402.552 | 4070.274 | 625.562 | 92 | 178 | 31.5 | 51 | 30.6 | 52.8 | 0 | 0 | - | - | 32.5 | 50.5 | 238 | 145 | 53.1 | 53 | 63.4 | 22.7 | 38.6 | 2.19 | 10.1 | 24 | 53.1 | 69.4 | 22.8 | 42.9 | 2.52 | 9.7 | 25.2 | 21.1 | 23.1 | 26.4 | 2.28 | 1.07 | 2.55 | 1.08 | 238 | 145 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:50:00 | 4148.12 | 94.68 | 797942.78 | 765360.1 | 43.1 | 342.914 | 4129.912 | 384.911 | 93 | 178 | 31.2 | 51.3 | 30.2 | 53.1 | 0 | 0 | - | - | 32.1 | 50.9 | 238 | 145 | 53.1 | 53.1 | 63.6 | 22.7 | 38.9 | 2.22 | 10.1 | 23.8 | 53.1 | 69.6 | 22.7 | 42.9 | 2.53 | 9.8 | 25.3 | 20.9 | 22.9 | 27 | 2.29 | 1.06 | 2.56 | 1.08 | 238 | 145 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 14:55:00 | 4184.3 | 94.68 | 797978.64 | 765360.1 | 43.8 | 320.551 | 4152.276 | 399.14 | 94 | 178 | 31.1 | 51.2 | 29.8 | 53.5 | 0 | 0 | - | - | 31.7 | 51.2 | 238 | 145 | 53.6 | 53.6 | 63.9 | 22.6 | 39.1 | 2.23 | 10 | 23.9 | 53.6 | 70.1 | 22.6 | 43.1 | 2.54 | 9.8 | 25.7 | 20.8 | 22.7 | 27.5 | 2.3 | 1.06 | 2.57 | 1.07 | 238 | 145 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:00:00 | 4194.94 | 95.08 | 797988.82 | 765360.5 | 44.49 | 283.278 | 4189.548 | 5.808 | 94 | 178 | 30.9 | 51.2 | 29.6 | 53.6 | 0 | 0 | - | - | 31.5 | 51.4 | 238 | 145 | 53.6 | 53.6 | 64.3 | 22.5 | 39.3 | 2.24 | 10 | 24.2 | 53.6 | 70.5 | 22.4 | 43.1 | 2.54 | 10 | 26 | 20.7 | 22.7 | 28.9 | 2.32 | 1.06 | 2.57 | 1.06 | 238 | 145 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:05:00 | 4195.16 | 95.78 | 797989.04 | 765361.2 | 45.17 | 268.368 | 4204.458 | -12.859 | 94 | 178 | 30.6 | 51.3 | 29.5 | 53.5 | 0 | 0 | - | - | 31.4 | 51.4 | 238 | 145 | 53.6 | 53.5 | 64.3 | 22.3 | 39.4 | 2.24 | 9.9 | 24 | 53.6 | 70.6 | 22.2 | 43.1 | 2.53 | 9.9 | 26.3 | 20.6 | 22.5 | 30 | 2.31 | 1.06 | 2.56 | 1.06 | 238 | 145 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:10:00 | 4195.16 | 96.84 | 797989.04 | 765362.28 | 45.89 | 268.368 | 4204.458 | -12.796 | 94 | 178 | 30.3 | 51.6 | 29.4 | 53.5 | 0 | 0 | - | - | 31.4 | 51.3 | 238 | 145 | 55.9 | 56.2 | 65 | 22.2 | 39.9 | 2.3 | 10.7 | 23.7 | 56.1 | 71 | 22.1 | 43.5 | 2.59 | 9.9 | 25.7 | 20.2 | 22.3 | 29.8 | 2.39 | 1.02 | 2.66 | 1.06 | 238 | 145 | 2979 | 2955
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:15:00 | 4195.16 | 98 | 797989.04 | 765363.42 | 46.85 | 290.733 | 4182.093 | -24.14 | 94 | 178 | 30 | 51.4 | 29.1 | 53.3 | 0 | 0 | - | - | 31.4 | 51.2 | 238 | 145 | 61.5 | 61.1 | 67.4 | 21.2 | 41.4 | 2.37 | 9.2 | 24.8 | 61.1 | 73.8 | 21.2 | 41.1 | 2.7 | 9.3 | 26.6 | 18.9 | 21.3 | 30.4 | 2.47 | 1.04 | 2.75 | 1.04 | 238 | 145 | 3132 | 3132
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:20:00 | 4195.16 | 99.04 | 797989.04 | 765364.46 | 47.82 | 298.188 | 4174.638 | -29.427 | 94 | 178 | 29.9 | 51.4 | 28.9 | 53.1 | 0 | 0 | - | - | 31.4 | 51 | 238 | 145 | 62 | 62.1 | 67.5 | 20.6 | 41.6 | 2.38 | 9.1 | 24.8 | 61.6 | 73.8 | 20.4 | 42.3 | 2.71 | 8.9 | 26.6 | 18.4 | 20.7 | 30.8 | 2.46 | 1.03 | 2.74 | 1.03 | 238 | 145 | 3132 | 3132
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:25:00 | 4195.16 | 100.1 | 797989.04 | 765365.56 | 48.81 | 298.188 | 4174.638 | -12.937 | 94 | 178 | 29.6 | 51.2 | 28.6 | 53 | 0 | 0 | - | - | 31.4 | 50.8 | 238 | 145 | 61.5 | 61.6 | 67.5 | 20.1 | 41.6 | 2.38 | 8.8 | 24.9 | 61.6 | 73.5 | 20.1 | 42.4 | 2.7 | 8.8 | 26.5 | 18.1 | 20.3 | 28.9 | 2.45 | 1.02 | 2.74 | 1.02 | 238 | 145 | 3132 | 3132
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:30:00 | 4195.16 | 101.2 | 797989.04 | 765366.68 | 49.77 | 298.187 | 4174.639 | -31.091 | 94 | 178 | 29.4 | 50.9 | 28.4 | 52.9 | 0 | 0 | - | - | 31.4 | 50.6 | 238 | 145 | 60.5 | 60.5 | 66.4 | 19.7 | 40.7 | 2.32 | 8.7 | 24.7 | 60.9 | 73 | 19.7 | 42 | 2.67 | 8.6 | 26.3 | 17.7 | 20 | 27.8 | 2.41 | 1.01 | 2.71 | 1.01 | 238 | 145 | 3132 | 3132
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:35:00 | 4195.26 | 102.32 | 797989.14 | 765367.74 | 50.74 | 313.097 | 4159.729 | -11.673 | 94 | 178 | 29.2 | 50.8 | 28.2 | 52.7 | 0 | 0 | - | - | 31.4 | 50.4 | 238 | 144 | 61.5 | 61.5 | 66.8 | 19.4 | 40.8 | 2.34 | 9 | 24.8 | 61.5 | 72.9 | 19.3 | 42.3 | 2.68 | 8.5 | 26.1 | 17.4 | 19.7 | 28.1 | 2.4 | 0.99 | 2.71 | 1.01 | 238 | 144 | 3132 | 3132
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:40:00 | 4195.26 | 103.3 | 797989.14 | 765368.72 | 51.7 | 283.278 | 4189.548 | -13.791 | 94 | 178 | 29 | 50.7 | 28 | 52.5 | 0 | 0 | - | - | 31.4 | 50.1 | 238 | 144 | 61.6 | 62 | 68 | 19.2 | 41.2 | 2.35 | 9.3 | 25.8 | 62 | 73.1 | 19.2 | 42.9 | 2.68 | 8.6 | 26.2 | 17.2 | 19.4 | 28.9 | 2.44 | 0.98 | 2.72 | 1 | 238 | 144 | 3132 | 3132
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:45:00 | 4195.26 | 104.12 | 797989.14 | 765369.54 | 52.52 | 275.823 | 4197.003 | -11.797 | 94 | 178 | 28.9 | 50.6 | 27.8 | 52.4 | 0 | 0 | - | - | 31.4 | 49.8 | 0 | 0 | 52.7 | 52.6 | 67.6 | 19 | 40.7 | 2.14 | 5.8 | 29.5 | 54.2 | 72.6 | 19 | 43.4 | 2.46 | 6.9 | 29.6 | 18.5 | 19.3 | 29.1 | 1.78 | 0.66 | 1.95 | 0.74 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:50:00 | 4195.26 | 105.16 | 797989.14 | 765370.64 | 52.77 | 290.733 | 4182.093 | -13.619 | 94 | 178 | 28.5 | 51.3 | 27.6 | 53.1 | 0 | 0 | - | - | 31.4 | 49.7 | 0 | 0 | 0 | 0 | 32.9 | 34.2 | 30.5 | 1.5 | 12.1 | 8.2 | 0 | 33 | 38.6 | 32.4 | 1.56 | 16.5 | 7.5 | 22.2 | 22.3 | 28.6 | 1.51 | 1.43 | 1.54 | 1.43 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 15:55:00 | 4195.26 | 106.36 | 797989.14 | 765371.78 | 53.03 | 320.551 | 4152.276 | -16.834 | 94 | 178 | 28.2 | 52.3 | 27.6 | 53.8 | 0 | 0 | - | - | 31.3 | 49.7 | 0 | 0 | 0 | 0 | 27.6 | 40.6 | 30.7 | 1.44 | 17.1 | 4.1 | 0 | 28.7 | 43.1 | 30.6 | 1.47 | 19.6 | 5.3 | 23.3 | 23.4 | 27.8 | 1.47 | 1.48 | 1.47 | 1.47 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:00:00 | 4195.28 | 107.34 | 797989.16 | 765372.8 | 53.26 | 313.097 | 4159.729 | -14.35 | 93 | 178 | 28 | 53 | 27.5 | 54.3 | 0 | 0 | - | - | 31.2 | 49.7 | 0 | 0 | 0 | 0 | 27.7 | 39.6 | 30.6 | 1.45 | 15.8 | 4.1 | 0 | 28.8 | 40.9 | 29.7 | 1.48 | 17.2 | 5.3 | 23.7 | 23.8 | 28.1 | 1.49 | 1.49 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:05:00 | 4195.28 | 108.42 | 797989.16 | 765373.86 | 53.49 | 298.188 | 4174.638 | -12.687 | 93 | 178 | 27.9 | 53.5 | 27.4 | 54.7 | 0 | 0 | - | - | 31.2 | 49.7 | 0 | 0 | 0 | 0 | 28 | 38.1 | 30.1 | 1.46 | 14 | 4.1 | 0 | 29.1 | 38.9 | 29.2 | 1.49 | 14.8 | 5.3 | 23.9 | 24.1 | 27.3 | 1.5 | 1.5 | 1.49 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:10:00 | 4195.28 | 109.5 | 797989.16 | 765374.94 | 53.68 | 313.098 | 4159.728 | -13.832 | 93 | 178 | 27.8 | 53.8 | 27.4 | 54.9 | 0 | 0 | - | - | 31.1 | 49.8 | 0 | 0 | 0 | 0 | 28 | 37.2 | 29.6 | 1.47 | 12.9 | 3.9 | 0 | 29.1 | 37.1 | 28.7 | 1.49 | 12.9 | 5.2 | 24.1 | 24.2 | 27.6 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:15:00 | 4195.28 | 110.56 | 797989.16 | 765375.98 | 53.87 | 313.098 | 4159.728 | -14.856 | 93 | 178 | 27.7 | 54.1 | 27.3 | 55.1 | 0 | 0 | - | - | 31 | 49.9 | 0 | 0 | 0 | 0 | 27.9 | 36.4 | 29.2 | 1.47 | 12.1 | 3.8 | 0 | 29.1 | 35.7 | 28.6 | 1.49 | 11.4 | 5.1 | 24.1 | 24.2 | 27.7 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:20:00 | 4195.28 | 111.64 | 797989.16 | 765377.06 | 54.04 | 313.098 | 4159.728 | -15.516 | 93 | 178 | 27.6 | 54.3 | 27.3 | 55.3 | 0 | 0 | - | - | 30.9 | 50 | 0 | 0 | 0 | 0 | 27.8 | 35.9 | 28.9 | 1.47 | 11.5 | 3.7 | 0 | 28.9 | 34.7 | 28.4 | 1.5 | 10.4 | 5 | 24.2 | 24.3 | 27.8 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:25:00 | 4195.28 | 112.8 | 797989.16 | 765378.22 | 54.2 | 328.006 | 4144.82 | -2.643 | 93 | 178 | 27.5 | 54.5 | 27.2 | 55.4 | 0 | 0 | - | - | 30.9 | 50.1 | 0 | 0 | 0 | 0 | 27.8 | 35.6 | 28.7 | 1.47 | 11.2 | 3.7 | 0 | 28.8 | 33.9 | 28.3 | 1.5 | 9.6 | 4.9 | 24.2 | 24.4 | 27.8 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:30:00 | 4195.34 | 113.82 | 797989.22 | 765379.26 | 54.35 | 313.098 | 4159.728 | -15.22 | 93 | 178 | 27.4 | 54.6 | 27.2 | 55.5 | 0 | 0 | - | - | 30.8 | 50.2 | 0 | 0 | 0 | 0 | 27.9 | 34.9 | 28.6 | 1.47 | 10.5 | 3.7 | 0 | 28.8 | 33.4 | 28.2 | 1.49 | 9 | 4.8 | 24.2 | 24.4 | 27.8 | 1.5 | 1.52 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:35:00 | 4195.34 | 114.92 | 797989.22 | 765380.38 | 54.49 | 328.006 | 4144.82 | -1.022 | 93 | 178 | 27.4 | 54.7 | 27.2 | 55.7 | 0 | 0 | - | - | 30.7 | 50.2 | 0 | 0 | 0 | 0 | 27.9 | 34.2 | 28.6 | 1.47 | 9.8 | 3.8 | 0 | 28.7 | 32.7 | 28.2 | 1.49 | 8.4 | 4.7 | 24.2 | 24.4 | 27.9 | 1.5 | 1.52 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:40:00 | 4195.34 | 115.94 | 797989.22 | 765381.4 | 54.62 | 313.098 | 4159.728 | -15.053 | 93 | 178 | 27.3 | 54.8 | 27.1 | 55.7 | 0 | 0 | - | - | 30.7 | 50.3 | 0 | 0 | 0 | 0 | 28.1 | 33.9 | 28.5 | 1.47 | 9.4 | 3.9 | 0 | 28.7 | 32.4 | 28.2 | 1.5 | 7.9 | 4.7 | 24.2 | 24.4 | 28 | 1.51 | 1.52 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:45:00 | 4195.34 | 117.06 | 797989.22 | 765382.52 | 54.75 | 313.098 | 4159.728 | -13.367 | 93 | 178 | 27.3 | 55 | 27.1 | 55.9 | 0 | 0 | - | - | 30.7 | 50.4 | 0 | 0 | 0 | 0 | 28.2 | 33.6 | 28.5 | 1.47 | 9.1 | 4.1 | 0 | 28.7 | 32.1 | 28.2 | 1.5 | 7.8 | 4.7 | 24.2 | 24.4 | 28.1 | 1.51 | 1.52 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:50:00 | 4195.34 | 118.64 | 797989.22 | 765384.52 | 54.88 | 328.006 | 4144.82 | -223.127 | 93 | 178 | 27.3 | 55 | 27.1 | 55.9 | 0 | 0 | - | - | 30.6 | 50.4 | 0 | 0 | 0 | 0 | 28.5 | 33.4 | 28.6 | 1.47 | 8.8 | 4.3 | 0 | 28.8 | 32.1 | 28.2 | 1.5 | 7.6 | 4.7 | 24.3 | 24.4 | 27.9 | 1.51 | 1.52 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 16:55:00 | 4195.34 | 142.26 | 797989.22 | 765408.52 | 55.01 | 328.006 | 4144.82 | -436.537 | 93 | 178 | 27.2 | 55.1 | 27 | 55.9 | 0 | 0 | - | - | 30.6 | 50.5 | 0 | 0 | 0 | 0 | 28.6 | 32.9 | 28.6 | 1.47 | 8.5 | 4.3 | 0 | 28.7 | 31.9 | 28.2 | 1.5 | 7.5 | 4.7 | 24.3 | 24.4 | 28.1 | 1.51 | 1.52 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:00:00 | 4195.34 | 202.6 | 797989.22 | 765471.14 | 55.15 | 439.827 | 4032.999 | -861.864 | 91 | 178 | 27.2 | 55.2 | 27 | 56 | 0 | 0 | - | - | 30.5 | 50.5 | 0 | 0 | 0 | 0 | 28.6 | 32.8 | 28.6 | 1.47 | 8.3 | 4.4 | 0 | 28.8 | 31.8 | 28.2 | 1.5 | 7.4 | 4.7 | 24.3 | 24.5 | 28.6 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:05:00 | 4195.34 | 276.44 | 797989.22 | 765543.08 | 55.27 | 536.736 | 3936.09 | -887.534 | 90 | 178 | 27.2 | 55.2 | 27 | 56.1 | 0 | 0 | - | - | 30.6 | 50.5 | 0 | 0 | 0 | 0 | 28.8 | 32.6 | 28.7 | 1.48 | 8 | 4.5 | 0 | 28.8 | 31.8 | 28.3 | 1.5 | 7.3 | 4.7 | 24.3 | 24.5 | 28.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:10:00 | 4195.34 | 348.44 | 797989.22 | 765615.14 | 55.41 | 618.741 | 3854.085 | -866.741 | 88 | 178 | 27.2 | 55.4 | 27.1 | 56.1 | 0 | 0 | - | - | 30.6 | 50.5 | 0 | 0 | 0 | 0 | 28.9 | 32.2 | 28.7 | 1.48 | 7.6 | 4.5 | 0 | 28.9 | 31.7 | 28.4 | 1.51 | 7.1 | 4.7 | 24.4 | 24.6 | 28.6 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:15:00 | 4195.34 | 419.98 | 797989.22 | 765686.34 | 55.55 | 670.92 | 3801.906 | -859.426 | 86 | 178 | 27.2 | 55.4 | 27.1 | 56.1 | 0 | 0 | - | - | 30.7 | 50.5 | 0 | 0 | 0 | 0 | 28.9 | 31.9 | 28.7 | 1.48 | 7.2 | 4.5 | 0 | 28.9 | 31.6 | 28.5 | 1.51 | 6.9 | 4.6 | 24.5 | 24.7 | 28.8 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:20:00 | 4195.34 | 492.46 | 797989.22 | 765758.72 | 55.69 | 752.925 | 3719.901 | -862.98 | 85 | 178 | 27.2 | 55.5 | 27.1 | 56.1 | 0 | 0 | - | - | 30.7 | 50.5 | 0 | 0 | 0 | 0 | 29.1 | 31.7 | 28.8 | 1.49 | 6.9 | 4.5 | 0 | 29 | 31.3 | 28.6 | 1.51 | 6.6 | 4.6 | 24.6 | 24.8 | 28.7 | 1.52 | 1.53 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:25:00 | 4195.34 | 563.76 | 797989.22 | 765831.02 | 55.83 | 805.104 | 3667.722 | -865.826 | 83 | 178 | 27.3 | 55.5 | 27.2 | 56.1 | 0 | 0 | - | - | 30.7 | 50.5 | 0 | 0 | 0 | 0 | 29.4 | 31.6 | 28.9 | 1.49 | 6.6 | 4.7 | 0 | 29.1 | 31.2 | 28.7 | 1.52 | 6.3 | 4.6 | 24.7 | 24.9 | 28.6 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:30:00 | 4195.34 | 636.96 | 797989.22 | 765903.7 | 55.98 | 894.564 | 3578.262 | -869.389 | 82 | 178 | 27.3 | 55.5 | 27.3 | 56.1 | 0 | 0 | - | - | 30.8 | 50.5 | 0 | 0 | 0 | 0 | 29.4 | 31.2 | 28.9 | 1.5 | 6.2 | 4.6 | 0 | 29.2 | 30.9 | 28.7 | 1.52 | 5.9 | 4.5 | 24.9 | 25 | 28.3 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:35:00 | 4195.34 | 708.26 | 797989.22 | 765975.02 | 56.13 | 954.202 | 3518.624 | -868.042 | 80 | 178 | 27.3 | 55.6 | 27.3 | 56.1 | 0 | 0 | - | - | 30.8 | 50.5 | 0 | 0 | 0 | 0 | 29.3 | 31.1 | 28.9 | 1.5 | 5.9 | 4.4 | 0 | 29.1 | 30.7 | 28.7 | 1.53 | 5.6 | 4.4 | 25 | 25.2 | 28.2 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:40:00 | 4195.34 | 781.14 | 797989.22 | 766047.94 | 56.29 | 1028.748 | 3444.078 | -867.904 | 78 | 178 | 27.3 | 55.7 | 27.4 | 56.1 | 0 | 0 | - | - | 30.8 | 50.5 | 0 | 0 | 0 | 0 | 29.2 | 30.8 | 28.9 | 1.51 | 5.5 | 4.2 | 0 | 29.1 | 30.6 | 28.8 | 1.53 | 5.3 | 4.2 | 25.1 | 25.3 | 28.4 | 1.54 | 1.55 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:45:00 | 4195.34 | 854.56 | 797989.22 | 766120.92 | 56.45 | 1110.751 | 3362.076 | -870.339 | 77 | 178 | 27.4 | 55.7 | 27.4 | 56.1 | 0 | 0 | - | - | 30.8 | 50.5 | 0 | 0 | 0 | 0 | 29.4 | 30.8 | 28.9 | 1.51 | 5.4 | 4.2 | 0 | 29.1 | 30.4 | 28.8 | 1.54 | 5.1 | 4.1 | 25.3 | 25.4 | 28.7 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:50:00 | 4195.34 | 926.78 | 797989.22 | 766193.52 | 56.61 | 1177.842 | 3294.984 | -874.538 | 75 | 178 | 27.4 | 55.8 | 27.5 | 56.1 | 0 | 0 | - | - | 30.8 | 50.6 | 0 | 0 | 0 | 0 | 29.5 | 30.8 | 29 | 1.52 | 5.3 | 4.2 | 0 | 29.2 | 30.4 | 28.9 | 1.54 | 5 | 4.1 | 25.4 | 25.5 | 28.6 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 17:55:00 | 4195.34 | 998.8 | 797989.22 | 766265.56 | 56.77 | 1267.3 | 3205.526 | -871.406 | 74 | 178 | 27.5 | 55.8 | 27.6 | 56.1 | 0 | 0 | - | - | 30.8 | 50.6 | 0 | 0 | 0 | 0 | 29.5 | 30.7 | 29 | 1.52 | 5 | 4.2 | 0 | 29.2 | 30.3 | 29 | 1.55 | 4.8 | 4.1 | 25.5 | 25.7 | 28.6 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:00:00 | 4195.34 | 1069.54 | 797989.22 | 766338.5 | 56.93 | 1319.481 | 3153.345 | -872.746 | 72 | 178 | 27.5 | 55.8 | 27.7 | 56.1 | 0 | 0 | - | - | 30.9 | 50.6 | 0 | 0 | 0 | 0 | 29.6 | 30.7 | 29 | 1.53 | 4.9 | 4 | 0 | 29.2 | 30.2 | 29 | 1.55 | 4.6 | 3.9 | 25.6 | 25.8 | 28.4 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:05:00 | 4195.34 | 1143.42 | 797989.22 | 766409.7 | 57.09 | 1416.396 | 3056.43 | -875.277 | 70 | 178 | 27.5 | 55.8 | 27.7 | 56.1 | 0 | 0 | - | - | 30.9 | 50.6 | 0 | 0 | 0 | 0 | 29.4 | 30.6 | 29 | 1.53 | 4.7 | 3.9 | 0 | 29.2 | 30.2 | 29.1 | 1.56 | 4.3 | 3.7 | 25.8 | 25.9 | 28.3 | 1.57 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:10:00 | 4195.34 | 1215.74 | 797989.22 | 766483.42 | 57.25 | 1476.032 | 2996.794 | -873.553 | 69 | 178 | 27.6 | 55.9 | 27.8 | 56.2 | 0 | 0 | - | - | 30.9 | 50.6 | 0 | 0 | 0 | 0 | 29.4 | 30.4 | 28.9 | 1.54 | 4.4 | 3.7 | 0 | 29.2 | 30.1 | 29.1 | 1.56 | 4.1 | 3.6 | 25.9 | 26 | 28.3 | 1.57 | 1.58 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:15:00 | 4195.34 | 1290.12 | 797989.22 | 766555.98 | 57.42 | 1558.034 | 2914.792 | -844.487 | 67 | 178 | 27.6 | 55.9 | 27.8 | 56.2 | 0 | 0 | - | - | 30.8 | 50.7 | 0 | 0 | 0 | 0 | 29.3 | 30.3 | 28.9 | 1.54 | 4.2 | 3.5 | 0 | 29.1 | 29.9 | 29.1 | 1.57 | 3.9 | 3.4 | 26 | 26.1 | 28.3 | 1.58 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:20:00 | 4195.34 | 1363.42 | 797989.22 | 766629.68 | 57.59 | 1625.124 | 2847.702 | -896.696 | 66 | 178 | 27.6 | 56 | 27.7 | 56.4 | 0 | 0 | - | - | 30.8 | 50.8 | 0 | 0 | 0 | 0 | 29.2 | 30.2 | 28.9 | 1.55 | 4.1 | 3.4 | 0 | 29.1 | 29.8 | 29.1 | 1.57 | 3.7 | 3.3 | 26.1 | 26.2 | 28.4 | 1.58 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:25:00 | 4195.34 | 1435.22 | 797989.22 | 766702.06 | 57.76 | 1707.129 | 2765.697 | -881.504 | 64 | 178 | 27.7 | 56 | 27.5 | 56.7 | 0 | 0 | - | - | 30.8 | 50.8 | 0 | 0 | 0 | 0 | 29.2 | 30.2 | 28.9 | 1.55 | 4 | 3.3 | 0 | 29.1 | 29.8 | 29.1 | 1.57 | 3.7 | 3.2 | 26.1 | 26.3 | 28.3 | 1.58 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:30:00 | 4195.34 | 1508.3 | 797989.22 | 766775.5 | 57.94 | 1781.674 | 2691.152 | -876.773 | 62 | 178 | 27.8 | 56 | 27.7 | 56.7 | 0 | 0 | - | - | 30.8 | 50.9 | 0 | 0 | 0 | 0 | 29.3 | 30.2 | 28.9 | 1.55 | 3.9 | 3.3 | 0 | 29 | 29.8 | 29.1 | 1.58 | 3.5 | 3.2 | 26.1 | 26.3 | 28.3 | 1.59 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:35:00 | 4195.34 | 1582.2 | 797989.22 | 766848.56 | 58.12 | 1856.223 | 2616.603 | -1100.27 | 61 | 178 | 27.8 | 56 | 27.9 | 56.3 | 0 | 0 | - | - | 30.7 | 51 | 0 | 0 | 0 | 0 | 29.3 | 30.2 | 28.9 | 1.55 | 3.9 | 3.2 | 0 | 29 | 29.8 | 29.1 | 1.58 | 3.5 | 3.1 | 26.2 | 26.3 | 28.3 | 1.59 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:40:00 | 4195.34 | 1673.36 | 797989.22 | 766941.02 | 58.3 | 1975.497 | 2497.329 | -1120.734 | 59 | 178 | 27.8 | 56 | 28 | 56.2 | 0 | 0 | - | - | 30.7 | 51.1 | 0 | 0 | 0 | 0 | 29.2 | 30.1 | 28.8 | 1.55 | 3.8 | 3.1 | 0 | 28.9 | 29.7 | 29.1 | 1.58 | 3.4 | 3 | 26.2 | 26.3 | 28.3 | 1.59 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:45:00 | 4195.34 | 1764.2 | 797989.22 | 767031.32 | 58.49 | 2057.5 | 2415.326 | -1105.96 | 57 | 178 | 27.8 | 56.1 | 28.2 | 56.2 | 0 | 0 | - | - | 30.7 | 51.1 | 0 | 0 | 0 | 0 | 29.2 | 30.1 | 28.9 | 1.55 | 3.7 | 3.1 | 0 | 28.9 | 29.7 | 29.1 | 1.58 | 3.4 | 3 | 26.2 | 26.3 | 28.3 | 1.59 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:50:00 | 4195.34 | 1860.54 | 797989.22 | 767128 | 58.69 | 2176.776 | 2296.05 | -1307.707 | 54 | 178 | 27.8 | 56.1 | 28.2 | 56.1 | 0 | 0 | - | - | 30.7 | 51.2 | 0 | 0 | 0 | 0 | 29.2 | 30.1 | 28.9 | 1.56 | 3.7 | 3.1 | 0 | 28.9 | 29.7 | 29.1 | 1.58 | 3.4 | 3 | 26.2 | 26.4 | 28.4 | 1.59 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 18:55:00 | 4195.34 | 1969.56 | 797989.22 | 767236.98 | 58.9 | 2296.05 | 2176.776 | -1322.62 | 52 | 178 | 27.9 | 56.1 | 28.3 | 56 | 0 | 0 | - | - | 30.7 | 51.2 | 0 | 0 | 0 | 0 | 29.2 | 30.1 | 29 | 1.56 | 3.7 | 3.1 | 0 | 29 | 29.7 | 29.1 | 1.58 | 3.3 | 3 | 26.3 | 26.4 | 28.5 | 1.59 | 1.6 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:00:00 | 4195.34 | 2088.26 | 797989.22 | 767358.44 | 59.13 | 2430.234 | 2042.592 | -1551.365 | 49 | 178 | 28 | 56 | 28.4 | 56 | 0 | 0 | - | - | 30.7 | 51.2 | 0 | 0 | 0 | 0 | 29.2 | 30.2 | 29.1 | 1.56 | 3.8 | 3.1 | 0 | 29 | 29.7 | 29.1 | 1.58 | 3.4 | 3 | 26.3 | 26.4 | 28.7 | 1.59 | 1.6 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:05:00 | 4195.34 | 2219.52 | 797989.22 | 767487.3 | 59.38 | 2549.513 | 1923.313 | -1530.569 | 46 | 178 | 27.8 | 56.3 | 28.3 | 56.2 | 0 | 0 | - | - | 30.7 | 51.3 | 0 | 0 | 0 | 0 | 29.4 | 30.3 | 29.2 | 1.56 | 3.7 | 3.2 | 0 | 29.1 | 29.8 | 29.2 | 1.59 | 3.3 | 3 | 26.4 | 26.5 | 28.7 | 1.6 | 1.61 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:10:00 | 4195.34 | 2348.24 | 797989.22 | 767616 | 59.65 | 2668.788 | 1804.038 | -1539.665 | 43 | 178 | 27.8 | 56.5 | 28.5 | 56.2 | 0 | 0 | - | - | 30.8 | 51.3 | 0 | 0 | 0 | 0 | 29.6 | 30.3 | 29.2 | 1.56 | 3.8 | 3.3 | 0 | 29.2 | 29.8 | 29.3 | 1.59 | 3.3 | 3 | 26.5 | 26.7 | 28.7 | 1.6 | 1.61 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:15:00 | 4195.34 | 2475.68 | 797989.22 | 767742.66 | 59.92 | 2802.972 | 1669.854 | -1546.192 | 40 | 178 | 28.1 | 56.2 | 28.9 | 55.7 | 0 | 0 | - | - | 30.8 | 51.3 | 0 | 0 | 0 | 0 | 29.7 | 30.4 | 29.3 | 1.57 | 3.7 | 3.3 | 0 | 29.3 | 29.8 | 29.3 | 1.6 | 3.2 | 3 | 26.7 | 26.8 | 28.9 | 1.6 | 1.62 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:20:00 | 4195.34 | 2614.92 | 797989.22 | 767882.16 | 60.2 | 2944.611 | 1528.215 | -1778.566 | 37 | 178 | 28.3 | 56.1 | 29.2 | 55.4 | 0 | 0 | - | - | 30.9 | 51.3 | 0 | 0 | 0 | 0 | 29.9 | 30.5 | 29.4 | 1.57 | 3.7 | 3.4 | 0 | 29.4 | 29.9 | 29.4 | 1.6 | 3.1 | 3 | 26.9 | 26.9 | 28.9 | 1.61 | 1.62 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:25:00 | 4195.34 | 2763.52 | 797989.22 | 768031.68 | 60.55 | 3078.795 | 1394.031 | -1798.642 | 34 | 178 | 28.5 | 55.9 | 29.4 | 55.2 | 0 | 0 | - | - | 30.9 | 51.3 | 144 | 141 | 0 | 0 | 33.2 | 29.4 | 29.6 | 1.99 | 7 | -1.7 | 0 | 32.4 | 28.8 | 29.6 | 2.04 | 6.1 | -3 | 25.9 | 27.2 | 29.1 | 2.44 | 1.02 | 2.6 | 1.11 | 208 | 167 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:30:00 | 4195.34 | 2913 | 797989.22 | 768183 | 61.23 | 3235.344 | 1237.482 | -1795.406 | 30 | 178 | 28.6 | 55.7 | 29.6 | 54.9 | 0 | 0 | - | - | 31 | 51.3 | 229 | 172 | 54.5 | 54.2 | 64.8 | 24.8 | 40.9 | 2.33 | 11.2 | 23 | 54.3 | 68.2 | 24.7 | 43.9 | 2.58 | 10.6 | 23 | 22.7 | 24.7 | 29.5 | 2.41 | 1.09 | 2.62 | 1.12 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:35:00 | 4195.34 | 3064.02 | 797989.22 | 768335 | 61.95 | 3391.895 | 1080.933 | -1820.745 | 27 | 178 | 28.7 | 55.5 | 29.8 | 54.5 | 0 | 0 | - | - | 31.1 | 51.2 | 229 | 172 | 55.3 | 55.4 | 65.9 | 23.8 | 40.1 | 2.3 | 11.1 | 24.6 | 55.3 | 70.1 | 23.7 | 44 | 2.59 | 9.7 | 24.8 | 22.1 | 23.9 | 29.4 | 2.36 | 1.07 | 2.62 | 1.11 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:40:00 | 4195.34 | 3215.66 | 797989.22 | 768483.88 | 62.67 | 3548.442 | 924.384 | -1821.083 | 23 | 178 | 28.8 | 55.3 | 29.9 | 54.2 | 0 | 0 | - | - | 31.2 | 51.2 | 229 | 172 | 55.8 | 55.9 | 66.9 | 23.7 | 40.7 | 2.33 | 10.9 | 25.1 | 55.8 | 70.7 | 23.7 | 44.3 | 2.6 | 9.8 | 25.2 | 21.9 | 23.8 | 29.8 | 2.37 | 1.07 | 2.63 | 1.11 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:45:00 | 4195.34 | 3369.68 | 797989.22 | 768638.94 | 63.38 | 3682.63 | 790.196 | -1874.224 | 20 | 178 | 28.9 | 55 | 30.1 | 54 | 0 | 0 | - | - | 31.2 | 51.2 | 229 | 172 | 55.8 | 55.9 | 66.4 | 23.7 | 40.2 | 2.29 | 10.9 | 25.4 | 55.8 | 70.5 | 23.7 | 44.2 | 2.6 | 9.6 | 25.1 | 22 | 24 | 29.3 | 2.37 | 1.07 | 2.62 | 1.12 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:50:00 | 4195.34 | 3513.26 | 797989.22 | 768781.1 | 64.11 | 3868.995 | 603.831 | -1555.954 | 15 | 178 | 29.1 | 54.8 | 30.3 | 53.7 | 0 | 0 | - | - | 31.3 | 51.1 | 229 | 172 | 55.9 | 55.9 | 66.5 | 24 | 40.5 | 2.32 | 10.9 | 25 | 55.9 | 70.8 | 24 | 44.4 | 2.6 | 9.7 | 25.3 | 22.3 | 24.3 | 29.8 | 2.39 | 1.08 | 2.64 | 1.12 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 19:55:00 | 4195.34 | 3628.6 | 797989.22 | 768897.46 | 64.82 | 3980.82 | 492.006 | -1348.165 | 12 | 178 | 29.3 | 54.6 | 30.5 | 53.5 | 0 | 0 | - | - | 31.4 | 51 | 229 | 172 | 55.1 | 55.4 | 65.8 | 24.2 | 39.6 | 2.26 | 11 | 25.2 | 55.3 | 70.3 | 24.2 | 44.2 | 2.59 | 9.5 | 25 | 22.5 | 24.5 | 28.6 | 2.33 | 1.09 | 2.62 | 1.14 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:00:00 | 4195.34 | 3718.94 | 797989.22 | 768988.6 | 65.52 | 4062.819 | 410.007 | -1055.604 | 10 | 178 | 29.5 | 54.4 | 30.5 | 53.5 | 0 | 0 | - | - | 31.5 | 51 | 229 | 172 | 55.1 | 54.9 | 65.5 | 24.4 | 39.6 | 2.27 | 11 | 24.9 | 54.8 | 69.9 | 24.4 | 44.1 | 2.59 | 9.6 | 24.5 | 22.7 | 24.7 | 28.4 | 2.34 | 1.09 | 2.62 | 1.15 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:05:00 | 4195.34 | 3811.52 | 797989.22 | 769079.6 | 66.24 | 4137.366 | 335.46 | -1065.943 | 8 | 178 | 29.7 | 54.2 | 30.6 | 53.5 | 0 | 0 | - | - | 31.5 | 51 | 229 | 172 | 55.1 | 54.9 | 65.6 | 24.5 | 39.8 | 2.27 | 11.1 | 24.9 | 54.8 | 69.8 | 24.5 | 44.1 | 2.59 | 9.5 | 24.5 | 22.8 | 24.8 | 28.5 | 2.34 | 1.09 | 2.62 | 1.15 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:10:00 | 4195.34 | 3878.52 | 797989.22 | 769145.14 | 66.95 | 4182.093 | 290.733 | -466.112 | 7 | 178 | 29.8 | 54.1 | 30.5 | 53.6 | 0 | 0 | - | - | 31.6 | 51 | 229 | 172 | 55.1 | 54.9 | 65.6 | 24.6 | 39.8 | 2.28 | 11.1 | 24.8 | 54.8 | 69.6 | 24.6 | 44.2 | 2.59 | 9.5 | 24.2 | 22.9 | 24.9 | 28.6 | 2.34 | 1.1 | 2.62 | 1.15 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:15:00 | 4195.34 | 3914.64 | 797989.22 | 769180.3 | 67.66 | 4204.458 | 268.368 | -261.85 | 7 | 178 | 29.9 | 54 | 30.4 | 53.7 | 0 | 0 | - | - | 31.6 | 51 | 229 | 172 | 55.6 | 55.9 | 66.3 | 24.6 | 40.5 | 2.32 | 11.2 | 24.7 | 55.7 | 70.1 | 24.6 | 44.4 | 2.61 | 9.6 | 24.4 | 22.8 | 24.8 | 29.2 | 2.39 | 1.1 | 2.64 | 1.15 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:20:00 | 4195.34 | 3936.42 | 797989.22 | 769202.32 | 68.37 | 4204.458 | 268.368 | -260.617 | 6 | 178 | 29.8 | 54.1 | 30.2 | 53.9 | 0 | 0 | - | - | 31.6 | 51 | 229 | 172 | 55.6 | 55.9 | 66.1 | 24.6 | 40.1 | 2.3 | 11.1 | 24.8 | 55.7 | 70.2 | 24.6 | 44.4 | 2.61 | 9.6 | 24.6 | 22.8 | 24.8 | 29.2 | 2.36 | 1.09 | 2.64 | 1.15 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:25:00 | 4195.34 | 3956.64 | 797989.22 | 769222.18 | 69.07 | 4234.278 | 238.548 | -243.296 | 6 | 178 | 29.7 | 54.2 | 30 | 54.2 | 0 | 0 | - | - | 31.6 | 51.1 | 229 | 172 | 55.7 | 55.8 | 66 | 24.4 | 39.9 | 2.27 | 11.1 | 25.2 | 55.7 | 70.4 | 24.3 | 44.4 | 2.6 | 9.5 | 24.9 | 22.7 | 24.7 | 28.9 | 2.35 | 1.09 | 2.63 | 1.14 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:30:00 | 4195.34 | 3976.74 | 797989.22 | 769242.66 | 69.77 | 4249.188 | 223.638 | -237.821 | 6 | 178 | 29.6 | 54.2 | 29.9 | 54.3 | 0 | 0 | - | - | 31.6 | 51.1 | 229 | 172 | 55.1 | 55.3 | 65.7 | 24.2 | 39.8 | 2.26 | 11 | 25.2 | 55.2 | 70.2 | 24.2 | 44.2 | 2.59 | 9.6 | 24.9 | 22.6 | 24.4 | 28.8 | 2.34 | 1.08 | 2.62 | 1.13 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:35:00 | 4195.34 | 4001 | 797989.22 | 769266.96 | 70.47 | 4249.188 | 223.638 | -13.228 | 5 | 178 | 29.6 | 54.1 | 29.7 | 54.4 | 0 | 0 | - | - | 31.6 | 51.1 | 229 | 172 | 55.1 | 54.8 | 65.5 | 24.1 | 39.7 | 2.27 | 10.9 | 24.8 | 55.2 | 69.9 | 24.1 | 44 | 2.59 | 9.6 | 24.7 | 22.3 | 24.3 | 29.1 | 2.34 | 1.08 | 2.62 | 1.13 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:40:00 | 4195.34 | 4002.5 | 797989.22 | 769267.92 | 71.16 | 4241.733 | 231.093 | -9.175 | 5 | 178 | 29.5 | 54.2 | 29.5 | 54.6 | 0 | 0 | - | - | 31.5 | 51.2 | 229 | 172 | 54.1 | 54.3 | 64.7 | 23.9 | 39.1 | 2.24 | 11 | 24.5 | 54.2 | 69.5 | 23.8 | 43.7 | 2.56 | 9.5 | 24.5 | 22.2 | 24.2 | 29.4 | 2.32 | 1.07 | 2.6 | 1.12 | 229 | 172 | 2400 | 2400
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:45:00 | 4195.34 | 4003.14 | 797989.22 | 769268.56 | 71.86 | 4241.733 | 231.093 | -9.964 | 5 | 178 | 29.4 | 54.2 | 29.3 | 54.8 | 0 | 0 | - | - | 31.5 | 51.2 | 229 | 172 | 55.1 | 54.8 | 65.5 | 23.7 | 39.8 | 2.27 | 11 | 24.9 | 54.7 | 69.9 | 23.7 | 43.9 | 2.58 | 9.7 | 24.8 | 21.9 | 23.9 | 30.3 | 2.34 | 1.07 | 2.61 | 1.11 | 229 | 172 | 2440 | 2440
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:50:00 | 4195.34 | 4004.02 | 797989.22 | 769269.46 | 72.7 | 4249.188 | 223.638 | -6.266 | 5 | 178 | 29.2 | 54 | 29.1 | 54.9 | 0 | 0 | - | - | 31.4 | 51.3 | 233 | 170 | 60.1 | 60.1 | 67.7 | 23.2 | 40.9 | 2.33 | 10.8 | 25.9 | 60.2 | 70.5 | 23.2 | 45 | 2.68 | 8.2 | 23.6 | 21.1 | 23.3 | 29.1 | 2.39 | 1.06 | 2.71 | 1.14 | 233 | 165 | 2866 | 2866
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 20:55:00 | 4195.4 | 4004.6 | 797989.28 | 769270.04 | 73.55 | 4241.733 | 231.093 | -9.856 | 5 | 178 | 29.1 | 53.9 | 29 | 54.8 | 0 | 0 | - | - | 31.4 | 51.3 | 233 | 154 | 59.6 | 59.6 | 67.4 | 22.6 | 40.5 | 2.31 | 10.5 | 26 | 59.7 | 70.4 | 22.5 | 44.6 | 2.66 | 8.3 | 23.9 | 20.6 | 22.8 | 28.4 | 2.37 | 1.04 | 2.69 | 1.11 | 233 | 151 | 2866 | 2866
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:00:00 | 4195.4 | 4005.04 | 797989.28 | 769270.5 | 74.42 | 4241.733 | 231.093 | -10.392 | 5 | 178 | 29 | 53.8 | 28.8 | 54.7 | 0 | 0 | - | - | 31.3 | 51.3 | 233 | 148 | 59.6 | 59.6 | 67.4 | 22.2 | 40.4 | 2.31 | 10.6 | 26 | 59.7 | 70.8 | 22.2 | 44.4 | 2.66 | 8.4 | 24.3 | 20.2 | 22.4 | 28.9 | 2.39 | 1.03 | 2.69 | 1.1 | 233 | 148 | 2866 | 2866
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:05:00 | 4196.38 | 4005.24 | 797990.4 | 769270.66 | 75.28 | 4241.733 | 231.093 | 42.755 | 5 | 178 | 28.9 | 53.7 | 28.6 | 54.7 | 0 | 0 | - | - | 31.3 | 51.3 | 233 | 143 | 59.6 | 59.6 | 67.4 | 21.8 | 40.3 | 2.3 | 10.5 | 26.1 | 59.2 | 70.9 | 21.8 | 44.1 | 2.64 | 8.6 | 24.6 | 19.9 | 22.1 | 28.3 | 2.38 | 1.02 | 2.68 | 1.09 | 233 | 143 | 2866 | 2866
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:10:00 | 4201.28 | 4005.24 | 797995.22 | 769270.66 | 76.14 | 4241.733 | 231.093 | 46.508 | 6 | 178 | 28.8 | 53.6 | 28.4 | 54.6 | 0 | 0 | - | - | 31.2 | 51.3 | 233 | 143 | 59.6 | 59.6 | 67.6 | 21.6 | 40.3 | 2.31 | 10.6 | 26.1 | 59.2 | 71 | 21.6 | 44.1 | 2.65 | 8.6 | 24.7 | 19.7 | 21.8 | 28.4 | 2.37 | 1.01 | 2.67 | 1.07 | 233 | 143 | 2866 | 2866
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:15:00 | 4201.96 | 4006.26 | 797995.84 | 769271.68 | 76.99 | 4204.458 | 268.368 | -16.298 | 6 | 178 | 28.6 | 53.4 | 28.3 | 54.5 | 0 | 0 | - | - | 31.2 | 51.2 | 233 | 143 | 59.1 | 59.6 | 67.8 | 21.3 | 40.4 | 2.29 | 10.5 | 26.6 | 59.2 | 71.1 | 21.2 | 44.1 | 2.63 | 8.8 | 25 | 19.4 | 21.6 | 29 | 2.37 | 1 | 2.67 | 1.06 | 233 | 143 | 2859 | 2859
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:20:00 | 4201.96 | 4007.62 | 797995.84 | 769273.06 | 77.84 | 4249.188 | 223.638 | -2.863 | 6 | 178 | 28.5 | 53.2 | 28.1 | 54.4 | 0 | 0 | - | - | 31.1 | 51.2 | 233 | 143 | 59.1 | 59.6 | 67.7 | 21.1 | 40.4 | 2.33 | 10.6 | 25.9 | 59.2 | 71.4 | 21.1 | 44.1 | 2.64 | 8.8 | 25.2 | 19.2 | 21.3 | 29.5 | 2.4 | 1 | 2.67 | 1.05 | 233 | 143 | 2859 | 2859
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:25:00 | 4201.96 | 4008.98 | 797995.84 | 769274.42 | 78.7 | 4249.188 | 223.638 | -14.002 | 6 | 178 | 28.4 | 53.1 | 27.9 | 54.3 | 0 | 0 | - | - | 31.1 | 51.1 | 233 | 143 | 59.6 | 59.6 | 68 | 20.8 | 40.5 | 2.31 | 10.5 | 26.5 | 59.2 | 71.6 | 20.8 | 44.1 | 2.63 | 8.7 | 25.6 | 18.9 | 21.1 | 29.6 | 2.38 | 0.99 | 2.66 | 1.04 | 233 | 143 | 2869 | 2869
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:30:00 | 4201.98 | 4010.24 | 797995.86 | 769275.68 | 79.58 | 4211.913 | 260.913 | -16.967 | 6 | 178 | 28.3 | 52.9 | 27.8 | 54.2 | 0 | 0 | - | - | 31 | 51.1 | 233 | 143 | 60.1 | 60.1 | 68.3 | 20.6 | 40.7 | 2.33 | 10.5 | 26.6 | 60.2 | 71.9 | 20.6 | 44.3 | 2.65 | 8.7 | 25.6 | 18.7 | 20.8 | 29.6 | 2.42 | 0.98 | 2.68 | 1.04 | 233 | 143 | 2935 | 2935
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:35:00 | 4201.98 | 4011.6 | 797995.86 | 769277.04 | 80.47 | 4249.188 | 223.638 | -19.171 | 6 | 178 | 28.2 | 52.8 | 27.6 | 54 | 0 | 0 | - | - | 30.9 | 51 | 233 | 140 | 60.6 | 60.6 | 68.8 | 20.2 | 40.7 | 2.31 | 10.4 | 27.3 | 60.8 | 71.9 | 20.2 | 44.1 | 2.65 | 8.5 | 25.6 | 18.3 | 20.4 | 29.1 | 2.39 | 0.98 | 2.68 | 1.03 | 233 | 140 | 2994 | 2994
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:40:00 | 4202.02 | 4013 | 797995.9 | 769278.42 | 81.37 | 4249.188 | 223.638 | -15.497 | 6 | 178 | 28.1 | 52.6 | 27.5 | 53.9 | 0 | 0 | - | - | 30.9 | 50.9 | 233 | 138 | 60.1 | 60.1 | 68.4 | 19.9 | 40.5 | 2.3 | 10.2 | 27.1 | 59.8 | 71.8 | 19.8 | 43.6 | 2.63 | 8.5 | 25.8 | 17.9 | 20.2 | 28.6 | 2.37 | 0.97 | 2.66 | 1.02 | 233 | 138 | 2979 | 2979
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:45:00 | 4202.04 | 4014.38 | 797995.92 | 769279.84 | 82.27 | 4249.188 | 223.638 | -15.768 | 6 | 178 | 28 | 52.3 | 27.3 | 53.7 | 0 | 0 | - | - | 30.8 | 50.8 | 233 | 137 | 58.6 | 58.5 | 67.4 | 19.6 | 39.9 | 2.28 | 9.9 | 26.4 | 58.7 | 71.4 | 19.6 | 43.1 | 2.61 | 8.6 | 25.7 | 17.7 | 19.9 | 27.9 | 2.37 | 0.97 | 2.66 | 1.01 | 233 | 137 | 3000 | 3000
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:50:00 | 4202.04 | 4015.78 | 797995.92 | 769281.2 | 83.16 | 4249.188 | 223.638 | -17.426 | 6 | 178 | 27.9 | 52.1 | 27.1 | 53.6 | 0 | 0 | - | - | 30.8 | 50.6 | 233 | 137 | 60.1 | 60 | 68.2 | 19.3 | 40.4 | 2.3 | 10.1 | 26.9 | 59.7 | 71.9 | 19.3 | 43.5 | 2.62 | 8.6 | 26 | 17.4 | 19.7 | 28.3 | 2.37 | 0.96 | 2.66 | 1 | 233 | 137 | 2931 | 2931
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 21:55:00 | 4202.04 | 4017.18 | 797995.92 | 769282.64 | 83.66 | 4249.188 | 223.638 | -17.075 | 6 | 178 | 27.9 | 51.9 | 27 | 53.7 | 0 | 0 | - | - | 30.8 | 50.6 | 0 | 0 | 0 | 0 | 60 | 20.1 | 32.2 | 1.66 | 10.5 | 31.9 | 0 | 64.3 | 20.8 | 34.4 | 1.83 | 7.1 | 33.5 | 20.4 | 20.6 | 27.8 | 1.63 | 1.31 | 1.73 | 1.35 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:00:00 | 4202.04 | 4018.58 | 797995.92 | 769284.06 | 83.85 | 4249.188 | 223.638 | -18.121 | 6 | 178 | 27.6 | 52.7 | 26.9 | 54.4 | 0 | 0 | - | - | 30.7 | 50.6 | 0 | 0 | 0 | 0 | 28.9 | 35.8 | 29.7 | 1.45 | 13.3 | 5.4 | 0 | 30.8 | 40.3 | 30.7 | 1.5 | 17.6 | 6.7 | 22.6 | 22.7 | 27.7 | 1.47 | 1.45 | 1.48 | 1.45 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:05:00 | 4202.04 | 4020.18 | 797995.92 | 769285.64 | 84.03 | 4249.188 | 223.638 | -49.713 | 6 | 178 | 27.4 | 53.5 | 26.8 | 54.9 | 0 | 0 | - | - | 30.6 | 50.6 | 0 | 0 | 0 | 0 | 26.7 | 39.1 | 30 | 1.44 | 15.6 | 3.5 | 0 | 28.7 | 41.7 | 29.7 | 1.47 | 18.2 | 5.4 | 23.4 | 23.5 | 27.4 | 1.47 | 1.48 | 1.47 | 1.48 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:10:00 | 4202.04 | 4022.08 | 797995.92 | 769287.54 | 84.2 | 4249.188 | 223.638 | -20.813 | 6 | 178 | 27.3 | 54.1 | 26.7 | 55.3 | 0 | 0 | - | - | 30.6 | 50.7 | 0 | 0 | 0 | 0 | 27.2 | 38.1 | 29.9 | 1.45 | 14.3 | 3.6 | 0 | 28.9 | 39.7 | 29.2 | 1.48 | 15.9 | 5.4 | 23.7 | 23.8 | 27.2 | 1.48 | 1.49 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:15:00 | 4202.04 | 4024 | 797995.92 | 769289.46 | 84.35 | 4256.643 | 216.183 | -23.298 | 6 | 178 | 27.2 | 54.5 | 26.7 | 55.6 | 0 | 0 | - | - | 30.5 | 50.8 | 0 | 0 | 0 | 0 | 27.8 | 36.9 | 29.7 | 1.46 | 12.8 | 4 | 0 | 29.2 | 37.9 | 28.8 | 1.48 | 14 | 5.6 | 23.9 | 24 | 27.3 | 1.49 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:20:00 | 4202.04 | 4025.94 | 797995.92 | 769291.42 | 84.5 | 4249.188 | 223.638 | -37.698 | 6 | 178 | 27 | 54.7 | 26.7 | 55.8 | 0 | 0 | - | - | 30.5 | 50.8 | 0 | 0 | 0 | 0 | 28.1 | 36.1 | 29.3 | 1.46 | 12 | 4.2 | 0 | 29.3 | 36.9 | 28.7 | 1.49 | 12.7 | 5.6 | 23.9 | 24.1 | 27.4 | 1.49 | 1.5 | 1.49 | 1.5 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:25:00 | 4202.04 | 4027.96 | 797995.92 | 769293.42 | 84.63 | 4249.188 | 223.638 | -24.205 | 6 | 178 | 27 | 54.9 | 26.6 | 56 | 0 | 0 | - | - | 30.4 | 50.9 | 0 | 0 | 0 | 0 | 27.9 | 36.1 | 29.2 | 1.46 | 11.9 | 4 | 0 | 29.2 | 36.1 | 28.6 | 1.49 | 11.8 | 5.4 | 24 | 24.2 | 27.2 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:30:00 | 4202.04 | 4030.04 | 797995.92 | 769295.5 | 84.76 | 4256.643 | 216.183 | -21.562 | 6 | 178 | 26.9 | 55.2 | 26.5 | 56.2 | 0 | 0 | - | - | 30.3 | 51 | 0 | 0 | 0 | 0 | 28 | 35.7 | 28.9 | 1.46 | 11.5 | 4 | 0 | 29.2 | 35.1 | 28.2 | 1.49 | 10.9 | 5.3 | 24.1 | 24.2 | 27.2 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:35:00 | 4202.04 | 4031.82 | 797995.92 | 769297.28 | 84.87 | 4256.643 | 216.183 | -23.103 | 6 | 178 | 26.8 | 55.4 | 26.4 | 56.4 | 0 | 0 | - | - | 30.3 | 51 | 0 | 0 | 0 | 0 | 28.1 | 35.1 | 28.7 | 1.47 | 10.8 | 4 | 0 | 29.1 | 34.1 | 28.2 | 1.49 | 9.9 | 5.2 | 24.1 | 24.2 | 27.3 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:40:00 | 4202.06 | 4033.5 | 797995.94 | 769298.94 | 84.99 | 4249.188 | 223.638 | -22.305 | 6 | 178 | 26.7 | 55.5 | 26.3 | 56.6 | 0 | 0 | - | - | 30.2 | 51.1 | 0 | 0 | 0 | 0 | 28.1 | 34.4 | 28.6 | 1.47 | 10.1 | 4 | 0 | 28.9 | 33.4 | 28.2 | 1.49 | 9.2 | 5 | 24.1 | 24.3 | 27.6 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:45:00 | 4202.06 | 4034.92 | 797995.94 | 769300.38 | 85.09 | 4256.643 | 216.183 | -20.264 | 6 | 178 | 26.6 | 55.6 | 26.3 | 56.6 | 0 | 0 | - | - | 30.1 | 51.2 | 0 | 0 | 0 | 0 | 28.1 | 33.9 | 28.3 | 1.47 | 9.5 | 4 | 0 | 28.8 | 32.9 | 28.1 | 1.49 | 8.6 | 4.9 | 24.1 | 24.3 | 27.5 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:50:00 | 4202.1 | 4035.68 | 797995.98 | 769301.14 | 85.2 | 4226.823 | 246.003 | -8.941 | 6 | 178 | 26.6 | 55.7 | 26.3 | 56.7 | 0 | 0 | - | - | 30.1 | 51.2 | 0 | 0 | 0 | 0 | 28 | 33.4 | 28.2 | 1.47 | 8.9 | 3.9 | 0 | 28.7 | 32.2 | 27.9 | 1.49 | 8 | 4.7 | 24.2 | 24.3 | 27.5 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 22:55:00 | 4202.1 | 4036.66 | 797995.98 | 769302.1 | 85.29 | 4256.643 | 216.183 | -10.396 | 5 | 178 | 26.5 | 55.8 | 26.2 | 56.7 | 0 | 0 | - | - | 30 | 51.3 | 0 | 0 | 0 | 0 | 28 | 32.9 | 28.1 | 1.47 | 8.6 | 3.9 | 0 | 28.7 | 31.8 | 27.9 | 1.49 | 7.5 | 4.7 | 24.2 | 24.3 | 27.9 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:00:00 | 4202.16 | 4037.52 | 797996.04 | 769302.98 | 85.38 | 4256.643 | 216.183 | -10.127 | 5 | 178 | 26.4 | 55.9 | 26.2 | 56.8 | 0 | 0 | - | - | 30 | 51.3 | 0 | 0 | 0 | 0 | 28.1 | 32.6 | 28.1 | 1.47 | 8.3 | 4 | 0 | 28.7 | 31.6 | 27.9 | 1.49 | 7.2 | 4.7 | 24.2 | 24.3 | 28.1 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:05:00 | 4202.16 | 4042.04 | 797996.04 | 769307.46 | 85.47 | 4256.643 | 216.183 | -10.808 | 5 | 178 | 26.4 | 56 | 26.2 | 56.8 | 0 | 0 | - | - | 29.9 | 51.4 | 0 | 0 | 0 | 0 | 28.1 | 32.4 | 28.1 | 1.47 | 8.1 | 4 | 0 | 28.7 | 31.3 | 27.9 | 1.5 | 7 | 4.7 | 24.2 | 24.3 | 28.1 | 1.5 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:10:00 | 4202.26 | 4042.82 | 797996.14 | 769308.28 | 85.56 | 4256.643 | 216.183 | -13.563 | 5 | 178 | 26.3 | 56.1 | 26.1 | 56.9 | 0 | 0 | - | - | 29.9 | 51.4 | 0 | 0 | 0 | 0 | 28.3 | 32.3 | 28.1 | 1.47 | 7.9 | 4.2 | 0 | 28.6 | 31.2 | 27.9 | 1.5 | 6.9 | 4.7 | 24.2 | 24.3 | 27.7 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:15:00 | 4202.26 | 4043.68 | 797996.14 | 769309.1 | 85.65 | 4249.188 | 223.638 | -21.445 | 5 | 178 | 26.4 | 56.1 | 26 | 57.1 | 0 | 0 | - | - | 29.9 | 51.5 | 0 | 0 | 0 | 0 | 28.6 | 32.4 | 28.3 | 1.47 | 8 | 4.4 | 0 | 28.8 | 31.3 | 27.9 | 1.5 | 7 | 4.9 | 24.2 | 24.4 | 27.6 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:20:00 | 4202.28 | 4044.46 | 797996.16 | 769309.88 | 85.74 | 4256.643 | 216.183 | -8.473 | 5 | 178 | 26.3 | 56.1 | 25.9 | 57.3 | 0 | 0 | - | - | 29.8 | 51.5 | 0 | 0 | 0 | 0 | 28.7 | 32.5 | 28.4 | 1.47 | 8.1 | 4.6 | 0 | 29 | 31.4 | 27.9 | 1.5 | 7.1 | 5 | 24.2 | 24.4 | 27.6 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:25:00 | 4202.32 | 4045.22 | 797996.2 | 769310.64 | 85.82 | 4264.098 | 208.728 | -30.208 | 5 | 178 | 26.3 | 56.2 | 26 | 57.2 | 0 | 0 | - | - | 29.8 | 51.5 | 0 | 0 | 0 | 0 | 28.8 | 32.4 | 28.5 | 1.47 | 8 | 4.6 | 0 | 29 | 31.4 | 27.9 | 1.5 | 7 | 5 | 24.2 | 24.4 | 27.4 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:30:00 | 4202.34 | 4046.04 | 797996.22 | 769311.46 | 85.9 | 4264.098 | 208.728 | -33.23 | 5 | 178 | 26.2 | 56.3 | 26 | 57.1 | 0 | 0 | - | - | 29.8 | 51.5 | 0 | 0 | 0 | 0 | 29 | 32.2 | 28.6 | 1.47 | 7.8 | 4.8 | 0 | 29.1 | 31.3 | 28 | 1.5 | 6.9 | 5.1 | 24.2 | 24.4 | 27.4 | 1.5 | 1.52 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:35:00 | 4202.44 | 4046.88 | 797996.32 | 769312.3 | 85.98 | 4256.643 | 216.183 | -9.33 | 5 | 178 | 26.2 | 56.4 | 26 | 57.1 | 0 | 0 | - | - | 29.7 | 51.6 | 0 | 0 | 0 | 0 | 28.9 | 31.9 | 28.6 | 1.47 | 7.5 | 4.8 | 0 | 28.9 | 31.2 | 28 | 1.5 | 6.8 | 5 | 24.2 | 24.4 | 27.5 | 1.51 | 1.52 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:40:00 | 4202.44 | 4047.64 | 797996.32 | 769313.06 | 86.06 | 4264.098 | 208.728 | -10.426 | 5 | 178 | 26.1 | 56.4 | 26 | 57.1 | 0 | 0 | - | - | 29.7 | 51.6 | 0 | 0 | 0 | 0 | 28.8 | 31.7 | 28.3 | 1.47 | 7.2 | 4.7 | 0 | 28.8 | 30.9 | 28 | 1.5 | 6.5 | 4.8 | 24.2 | 24.4 | 27.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:45:00 | 4202.44 | 4048.42 | 797996.32 | 769313.86 | 86.13 | 4264.098 | 208.728 | -10.44 | 5 | 178 | 26.1 | 56.4 | 26 | 57.1 | 0 | 0 | - | - | 29.7 | 51.6 | 0 | 0 | 0 | 0 | 28.7 | 31.3 | 28.2 | 1.47 | 6.9 | 4.5 | 0 | 28.7 | 30.8 | 28 | 1.5 | 6.4 | 4.6 | 24.3 | 24.4 | 27.7 | 1.5 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:50:00 | 4202.5 | 4049.4 | 797996.38 | 769314.82 | 86.21 | 4264.098 | 208.728 | -9.234 | 5 | 178 | 26.1 | 56.4 | 26 | 57.1 | 0 | 0 | - | - | 29.6 | 51.7 | 0 | 0 | 0 | 0 | 28.6 | 31.1 | 28.1 | 1.47 | 6.6 | 4.4 | 0 | 28.6 | 30.6 | 28 | 1.5 | 6.2 | 4.5 | 24.3 | 24.4 | 27.6 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Pursat 400MWh-02 | / | B16-SmartLogger/B16-ESS01 | 2026-06-02 23:55:00 | 4202.54 | 4050.16 | 797996.42 | 769315.58 | 86.29 | 4264.098 | 208.728 | -9.433 | 5 | 178 | 26.1 | 56.5 | 26 | 57.1 | 0 | 0 | - | - | 29.6 | 51.7 | 0 | 0 | 0 | 0 | 28.6 | 30.8 | 28.1 | 1.47 | 6.3 | 4.3 | 0 | 28.4 | 30.4 | 27.9 | 1.5 | 6 | 4.4 | 24.3 | 24.4 | 27.7 | 1.51 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0